## RTD transmitter
Calibration Certificate: RTD temperature transmitter calibration with multifunction calibrator
Calibration certificate No.: 63- TI-1932 -0356 | [13 empty] | Page: 1/1
Service Request / Work Order No.: |  |  |  | 73976567
Description identification of instrument to be calibrated
Name: RTD temperature transmitter calibration with multifunction calibrator | [7 empty] | Tag no |  |  | 63- TT-1951
Sl. No.:153456689 | [7 empty] | Make: |  |  | Rosemount
Model / Type No.: 3144 / RTD input | [7 empty] | Range: |  |  | -10 to 110oC
Sensor: RTD sensor input | [7 empty] | Resolution: |  |  | 0.01 mA
Location: Cooling water tank outlet temperature transmitter in WTP
Applicable specification of instrument to be calibrated: Accuracy / permissible limit: | [9 empty] | 1%
Date of receipt of item: |  |  | 2023-03-30 |  |  |  | Date of calibration: |  |  |  | 2023-03-30
Calibration valid upto: |  |  | 2024-03-30 |  |  |  | Frequency of calibration: |  |  |  | 12 months
Environmental condition during calibration |  |  | Temperature: |  |  | 28°C ± 2°C
|  |  | Humidity: |  |  | 64% RH
Details of standard instruments Used:
Name of the instrument |  | Sr.No |  |  | Make/Model |  |  | Valid up to |  |  |  | Report no: / Certificate no:
Multifunction process calibrator |  | 1234598 |  |  | FLuke / 725 |  |  | 2023-11-08 |  |  |  | 1234STRW932
Mutlimeter |  | 765123 |  |  | Fluke / 87A |  |  | 2023-09-10 |  |  |  | 2022STR0209
475 field communicator |  | H1988R5 |  |  | Emerson/ 475 |  |  | 2023-08-10 |  |  |  | 2022STR0129
Basis of calibration: |  |  | Comparision with standards
Applied Procedure no : XXTG16134
Input in % | As found |  |  | As left |  |  |  |  | Expected Output(mA) |  | Error (OC) |  | Error in %
| Input(OC) | Output(mA) |  | Input(OC) |  |  | Output(mA)
0 | -10 | 4.1 |  | -10 |  |  | 4 |  | 4 |  | 0 |  | 0
25 | 20 | 8.1 |  | 20 |  |  | 8.01 |  | 8 |  | -0.01 |  | -0.0625
50 | 50 | 12.1 |  | 50 |  |  | 12.01 |  | 12 |  | -0.01 |  | -0.0625
75 | 80 | 16.1 |  | 80 |  |  | 16.01 |  | 16 |  | -0.01 |  | -0.0625
100 | 110 | 20.1 |  | 110 |  |  | 20 |  | 20 |  | 0 |  | 0
75 | 80 | 16.1 |  | 80 |  |  | 16 |  | 16 |  | 0 |  | 0
50 | 50 | 12.1 |  | 50 |  |  | 12 |  | 12 |  | 0 |  | 0
25 | 20 | 8.1 |  | 20 |  |  | 8.01 |  | 8 |  | -0.01 |  | -0.0625
0 | -10 | 4.1 |  | -10 |  |  | 4 |  | 4 |  | 0 |  | 0
Remarks: Calibration done and all the output values are with in the acceptable limit. Maximun as left error was 0.01 mA
Calibrated by | [6 empty] | Checked & approved by
Name: XXXXXXXXX | [6 empty] | Name: xxxxxxxxxxxxxx
Signature: | [6 empty] | Signature:
Date:30/3/2023 | [6 empty] | Date: 30/3/2023