## SplitRange
SPLIT RANGE CALCULATOR UPTO 3 SPLITS
No | Low Range | High Range | m | C | SPLIT 1 (0-50) |  |  |  | SPLIT 2 (50-75) |  |  |  | SPLIT 3 (75-100)
Split 1 | 0 | 50 | 2 | 0 | Y | m | X | C | Y | m | X | C | Y | m | X | C
Split 2 | 50 | 75 | 4 | -200 | 0 | 2 | 0 | 0 | 0 | 4 | 50 | -200 | 0 | 4 | 75 | -300
Split 3 | 75 | 100 | 4 | -300 | 10 | 2 | 5 | 0 | 10 | 4 | 52.5 | -200 | 10 | 4 | 77.5 | -300
Note - Only enter values in yellow area Formula used is Y= mX+C m & C is automatically calculated Where Y = Valve output as per PID output m = Gain in Fanout block Individual output tab X = PID output C = Output Bias in Fanout block Individual output tab |  |  |  |  | 20 | 2 | 10 | 0 | 20 | 4 | 55 | -200 | 20 | 4 | 80 | -300
[5 empty] | 30 | 2 | 15 | 0 | 30 | 4 | 57.5 | -200 | 30 | 4 | 82.5 | -300
[5 empty] | 40 | 2 | 20 | 0 | 40 | 4 | 60 | -200 | 40 | 4 | 85 | -300
[5 empty] | 50 | 2 | 25 | 0 | 50 | 4 | 62.5 | -200 | 50 | 4 | 87.5 | -300
[5 empty] | 60 | 2 | 30 | 0 | 60 | 4 | 65 | -200 | 60 | 4 | 90 | -300
[5 empty] | 70 | 2 | 35 | 0 | 70 | 4 | 67.5 | -200 | 70 | 4 | 92.5 | -300
[5 empty] | 80 | 2 | 40 | 0 | 80 | 4 | 70 | -200 | 80 | 4 | 95 | -300
[5 empty] | 90 | 2 | 45 | 0 | 90 | 4 | 72.5 | -200 | 90 | 4 | 97.5 | -300
[5 empty] | 100 | 2 | 50 | 0 | 100 | 4 | 75 | -200 | 100 | 4 | 100 | -300
AutomationForum.Co

## Sheet1
S.No | Calculator
1 | Flow Rate Calculation of Venturi_Orifice and Flow Nozzle SI units
2 | Flow Rate Calculation of Venturi_Orifice and Flow Nozzle US units
4 | Extended High and Low Limit Calculator
5 | 239896459-Level-Transmitter-Calc-Sheets
6 | mA to EU to V (5 No.s)
7 | Restriction Orifice Diamater Calculation