## Factory Acceptance Test (FAT) E
Factory Acceptance Test (FAT) Checklist for Marshalling Cabinet
Step | Inspection/Testing | Criteria | Status (Pass/Fail) | Remarks
Step 1 | Visual Inspection
1.1 | Cabinet structure integrity and alignment | No physical damage, proper door alignment
1.2 | Surface finish and paint quality | As per project specification, no chipping or corrosion
1.3 | Nameplates, labels, and terminal markings | Correct labeling as per drawings, securely fixed, legible
1.4 | Grounding and bonding | Securely connected to grounding bar, proper wire gauge used
1.5 | Component placement | Matches approved layout, correct orientation, secured properly
1.6 | Presence of surge protection devices | Installed and functional
1.7 | Verification of ventilation fans | Installed at correct locations, operational, airflow unobstructed
Step 2 | Mechanical Inspection
2.1 | Door and panel operation | Smooth opening/closing, proper locking mechanisms
2.2 | Cable entry points | Glands properly secured, no gaps, correct IP rating
2.3 | Mounting and fixing of components | Securely attached, no loose parts
2.4 | Edges and assembly | No sharp edges, properly aligned
Step 3 | Electrical Inspection
3.1 | Wiring matches schematics | No deviations from drawings
3.2 | Terminal tightness | Checked with torque wrench, meets specifications
3.3 | Presence of ferrules, tags, markers | Properly labeled and installed
3.4 | Grounding of modules and power supplies | Properly bonded and tested
3.5 | Fuse and MCB ratings | Correct selection as per design
3.6 | Redundant power supply testing | Power failover test conducted successfully
Step 4 | Continuity & Insulation Resistance Tests
4.1 | Continuity check | Verified using a multimeter
4.2 | Insulation resistance test | Conducted using Megger, meets resistance values
4.3 | Grounding integrity test | Earth resistance within acceptable range
4.4 | Shield continuity for signal cables | Proper shielding verified
Step 5 | Functional Testing
5.1 | Power application test | Correct voltage levels at all terminals
5.2 | Interface and PLC module test | Proper signal transmission and operation
5.3 | Communication protocol test | Modbus, Profibus, Ethernet/IP verified
5.4 | Alarm and trip circuits | Functional, correct response to failures
5.5 | Safety interlocks and fail-safe mechanisms | Operate as intended under fault conditions
Step 6 | Communication & Signal Testing
6.1 | Signal transmission to control system | Signals correctly received and processed
6.2 | Analog and digital I/O verification | Accuracy and range checks
6.3 | Signal loop testing | Complete end-to-end verification
Step 7 | Power-Up & Load Test
7.1 | Load simulation | Stable operation under rated load
7.2 | Thermal imaging | No overheating, heat dissipation effective
7.3 | Fan operation and noise levels | Normal noise levels, no abnormal vibrations
Step 8 | Final Inspection & Documentation
8.1 | Test report review | Complete and accurate, all steps documented
8.2 | As-built documentation verification | Matches physical installation
8.3 | Calibration certificate verification | Instruments used in FAT have valid calibration
Step 9 | Acceptance Criteria
9.1 | Compliance with approved drawings | No deviations
9.2 | Electrical & functional tests passed | Meets all performance requirements
Step 10 | Test Report & Sign-Off
10.1 | FAT report generation | Includes checklists, results, photos, and signatures
10.2 | Stakeholder sign-off | Manufacturer, customer, and inspector approval
Done By
Verified By