## Instrumentation JB Wiring and T
Instrumentation JB Wiring and Termination Checklist (Process Industries)
No. | Checklist Item & Description | Checkpoint Explanation | Reference Step | ✔ Check
1 | JB Location Verified as per Instrument Layout | Ensure installed JB matches the location shown in the IFC drawing. Must be accessible, vertical, and away from vibration. | Step 1 | ☐
2 | JB Label Fixed and Legible | Check for weatherproof, permanent labels (SS tag or laser-marked). Should match JB schedule and be visible. | Step 2 | ☐
3 | JB Enclosure Type Verified (Area Classification) | Confirm JB is rated for hazardous or safe area (e.g., Ex d for Zone 1, IP66 for outdoors). Material like SS316 or GRP is used. | Step 3 | ☐
4 | Proper JB Mounting and Mechanical Support | Rigidly fixed, upright, not exposed to walkways or excessive heat. No tilting or vibration allowed. | Step 4 | ☐
5 | Cable Glanding Type and Tightness Checked | Correct Ex glands for area type, proper clamping of armor, and unused entries plugged. | Step 5 | ☐
6 | Minimum Clearance for Safe Access Verified | 600 mm minimum clearance in front of JB, reachable without scaffolding. | Step 6 | ☐
7 | Internal/External Earth Studs Bonded and Tagged | Check for earth studs, crimped lugs, and bonding of gland plate. Test for continuity (<1 ohm). | Step 7, 20 | ☐
8 | Cable Shielding Grounded as per Design | Grounded at one end (typically DCS side); isolate in JB unless specified. Neatly dressed and tagged. | Step 8, 19 | ☐
9 | Unused Cable Gland Holes Sealed with Certified Stoppers | All spare entries sealed with certified IP66/Ex d plugs to prevent dust, gas, insect entry. | Step 9 | ☐
10 | Cable Core Termination Matches Drawing | Check ferrules, color coding, numbering, and terminal matching with loop diagram. | Step 10 | ☐
11 | Terminal Numbering Permanent and Identifiable | All terminal blocks labeled clearly using engraved tags or clip-on markers. | Step 11 | ☐
12 | Cable Lugs Type and Crimping Verified | Use approved ring/fork lugs, crimped with ratchet tool. No soldering allowed. | Step 12 | ☐
13 | Internal and External Cable Routing Proper | Segregated by signal type, tied with UV-rated ties, no stress or sharp bends. | Step 13 | ☐
14 | As-Built Drawing & Termination Schedule Updated | Ensure all field changes are updated in loop diagrams and marked "As-Built" with revision. | Step 14 | ☐
15 | Ingress Protection (IP/Ex) Confirmed - Doors, Gaskets, Seals Intact | JB must be IP65/IP66 rated, with intact door gaskets and tight sealing to prevent water/dust entry. | Step 15 | ☐
16 | Drain/Breather Plug Installed (if required) | For outdoor/corrosive areas, check if breather is fitted at JB bottom to release condensate. | Step 15 | ☐
17 | Silica Gel Pouch Inside JB | Check that desiccant is present (for moisture control) and within expiry or maintenance interval. | Step 15 | ☐
18 | Proper Segregation of AI, AO, DI, DO, Power | Ensure different signal types are terminated in separate strips or compartments with dividers. | Step 16 | ☐
19 | Internal Wire Management Neat and Accessible | All wires tagged, routed neatly, no overlaps, secured in cable duct or tie mounts. | Step 17 | ☐
20 | Spare Terminals/Cables Labeled and Terminated Properly | All spares tagged clearly, terminated, and dressed — not left loose inside JB. | Step 18 | ☐
21 | EMC Practices Followed (Separation & Shielding) | Signal vs power >300 mm apart. Twisted pair used for analog. Shielded cable terminations per EMC rules. | Step 19 | ☐
22 | Loop Continuity and IR Test Performed | Multimeter used to check continuity (<2 ohm); Megger for insulation test (>1 MΩ @500V DC). | Step 21 | ☐
23 | Terminal Tightness Verified with Torque Tool | Each terminal tightened with calibrated torque screwdriver as per terminal rating. | Step 22 | ☐
24 | Terminal Loading Within Rated Capacity | Ensure no overloading of terminals or jumpers. Refer to JB datasheet/current capacity. | Step 23 | ☐
25 | Smart JB Diagnostics Checked (if applicable) | LED health status OK, address setup correct, communication with host (for FF or HART). | Step 24 | ☐
26 | JB Cover Closed, Sealed and Tamper-Proofed | Cover screws tightened evenly, gasket compressed, tamper sticker or seal applied if required. | Step 25 | ☐
Remarks:
Checked by:
Validated by: