## Cable Gland Selection Checklist
Cable Gland Selection Checklist for Hazardous Area Installations
Checklist Category | Inspection Point | ✔️ Checked | Remarks
1. Cable Type Verification | Is the cable armored or unarmored?
Is the armour type identified (SWA, AWA, etc.)?
Is the cable bedding extruded and compact?
Are any fillers hygroscopic or flammable?
2. Gland Type Selection | Does the gland match the cable’s armour type?
Is the correct gland type selected (A, B, C, D, E, E1, E2)?
Is the gland certified for use in Ex environments?
3. Sizing & Fitment | Has the actual cable OD been measured using calipers?
Does the gland fit precisely without fillers or tapes?
Has the manufacturer's sizing chart been used?
4. Explosion Protection Compliance | Does the gland match or exceed the enclosure’s Ex rating (d, e, nR, i, p)?
Is the gland Ex d rated if connected to Ex d equipment?
Are hybrid Ex d/Ex t requirements met for dust zones?
5. Barrier Gland Requirement | Is the cable round and compact with bedding?
Is there any risk of gas path through fillers or strands?
Is the cable less than 3 meters long in Ex d?
Has a compound-sealed barrier gland been installed where required?
6. Ingress Protection (IP) | Is the gland rated IP66 or IP68 as required?
Is the sealing washer included and certified with the gland?
Has the gland been torque tightened per manufacturer spec?
7. Temperature Rating | Does the gland withstand ambient min/max temps of equipment?
Has the whole assembly (cable + gland + enclosure) been rated together?
8. Material and Corrosion Resistance | Are gland and enclosure metals compatible (avoid bi-metal corrosion)?
Is nickel plating ≥10 µm for brass glands?
Is 316L stainless steel used in corrosive or offshore areas?
9. EMC Requirements | Is EMC shielding required (e.g., for VFD or instrument cables)?
Is the EMC gland maintaining 360° contact without IP compromise?
10. Certification & Documentation | Are all glands ATEX / IECEx certified?
Are IP & Ex markings clearly visible on the gland body?
Is documentation (certificates, torque data, IP rating) available on file?
11. Installation & Inspection | Are all gland components installed correctly as per datasheet?
Is there visual access for inspection and retightening?
Are torque and inspection records maintained as per IEC 60079-17?
Checked by
verified by