## Fire alarm panel Battery calcul
Fire Alaram Battery Size Calculator
Entries only to be made in the Blue cell locations
Parameter | Number of Zone / Hooters |  | Current (Amps) |  | Total Current (Amps)
Quiescent Current |  |  |  |  | 0.06
IDC Standby Current | 2 | X | 0.0068 | = | 0.0136
Total Current in Normal Condition | 0.0736
Alarm Current | 0.4 | X | 0.035 | = | 0.014
No. of Sounder | 2 | X | 0.2 | = | 0.4
No. Strobe Cum Sounder | 2 | X | 0.1 | = | 0.2
No. of other Sounder | 2 | X | 0.05 | = | 0.1
Total Current in Alarm Condition | 0.714
Hours
Normal Condition | 1 | X | 0.0736 | = | 0.0736
Alarm Condtion | 3 | X | 0.714 | = | 2.142
SUM COLUMN FOR STANDBY LOAD |  |  | 2.6587 | = | AMPS
The user is entirely accountable for confirming these calculations because the current draws indicated here are subject to change.
Note on D12: No. Of Zones?
Note on D16: No. Of Zones?