## Intrinsically Safe Cable Select
Intrinsically Safe Cable Selection Checklist for EPC Engineers
S.No. | Category | Checklist Item | Verification | Remarks
1 | Zone Classification | Confirm hazardous area classification (Zone 0 / Zone 1 / Zone 2) from HAC drawings. | ☐
|  | Use only ATEX/IECEx certified cables for Zone 0 & Zone 1. | ☐
|  | Ensure cable sheath is blue for IS identification. | ☐
2 | System Parameters | Calculate total loop capacitance (Ccable + Cdevice). | ☐
|  | Calculate total loop inductance (Lcable + Ldevice). | ☐
|  | Confirm maximum allowable cable length from barrier datasheet. | ☐
|  | Check outer sheath: Polyurethane / halogen-free flame retardant. | ☐
3 | Cable Construction | Verify shielding (foil or copper braid) for instrumentation and communication circuits. | ☐
|  | Conductor material: Tinned/fine-stranded copper. | ☐
|  | Ensure compliance with flame spread and smoke emission standards (IEC 60332, IEC 61034). | ☐
4 | Environmental Conditions | Confirm temperature rating of cable (e.g., -40°C to +90°C). | ☐
|  | Check chemical resistance (oil, acids, solvents). | ☐
|  | Assess mechanical stress: armored/reinforced for mining, drilling, or conveyors. | ☐
|  | Verify UV resistance & water-blocking for outdoor/offshore installations. | ☐
5 | Cable Type & Application | Select Control Cables for low-voltage analog signals (4–20 mA loops). | ☐
|  | Use Multiconductor Cables for multi-device runs. | ☐
|  | Choose PLTC (Power-Limited Tray Cables) for fixed hazardous area installations. | ☐
|  | Specify Fieldbus/Profibus/Modbus IS variants for digital networks. | ☐
6 | Installation Best Practices | Maintain separation between IS and non-IS cables (as per IEC/NEC/ATEX). | ☐
|  | Use ATEX-certified glands and terminations. | ☐
|  | Avoid unnecessary loops or excess lengths. | ☐
|  | Route cables in dedicated IS trays or conduits, properly labeled. | ☐
|  | Include inspection & testing plan (continuity, insulation resistance, visual checks). | ☐
7 | Certification & Documentation | Check cable certification (ATEX, IECEx, UL, CSA, FM) based on project location. | ☐
|  | Verify cable datasheet for electrical & mechanical parameters. | ☐
|  | Ensure cable supplier provides DoC (Declaration of Conformity). | ☐
Verified by:
Validated by: