## Local Instrument Installation C
Local Instrument Installation Checklist (EPC & Commissioning Guide)
S. No | Checklist Item | Detailed Description | ✔️ Check
1 | Instrument Tag Number Verified | Ensure tag matches P&ID, loop diagram, and instrument index. Must be permanent, weatherproof, and clearly visible from operational side. | ☐
2 | Correct Instrument Type Installed | Verify the model, range, signal type (e.g., 4–20mA, HART), and datasheet compliance. Avoid substitutions. | ☐
3 | Installed as per Hook-Up Drawing | Check all fittings, supports, and accessories against approved hook-up drawings. No deviation without approval. | ☐
4 | Instrument Orientation Checked | Verify correct vertical or horizontal installation as per vendor manual. Avoid tilted or reversed mountings. | ☐
5 | Welds and Fittings Are Leak-Free | Inspect all threaded and welded joints for leaks. Conduct soap bubble or pneumatic leak tests. | ☐
6 | Root Valve Functionality Verified | Check for smooth open/close function. Valve type, handle access, and lockout confirmed. | ☐
7 | Manifold Orientation and Locking | Ensure HP/LP side connections are correct. All bolts tight and tamper-proof lock provided. | ☐
8 | Impulse Line Slope and Support | Maintain proper slope (1:10). Use clamps every 1–1.5 meters. Avoid sharp bends or rubbing. | ☐
9 | Drain/Vent Plugs Are Sealed | Seal all unused ports properly. Use approved plugs and sealant. Vent direction must be safe. | ☐
10 | Instrument Grounding Provided | Ground via green-yellow cable to dedicated point. Avoid ground loops. Resistance <1Ω. | ☐
11 | Cable Gland and Termination Completed | Install IP-rated glands. Terminate cables with ferrules and number both ends. Shield grounded one end only. | ☐
12 | Weather Protection Ensured | Verify sunshields, rain hoods, or splash covers installed. Enclosure IP/NEMA rating adequate. | ☐
13 | Instrument Location Matches GA Drawing | Location should match coordinates in layout. Ensure easy access and tag visibility. | ☐
14 | SS Tag Plate Fixed on Instrument | Use SS304/316 tags, fastened with SS wire/rivets. Clear readable font and corrosion-proof. | ☐
15 | Tubing Material and Bending Radius Verified | Use seamless SS316 tubing. Check wall thickness. Use tube bender for proper radius. | ☐
16 | Calibration Sticker Applied | Sticker must show calibration/due date and technician ID. Must be weatherproof and non-obstructive. | ☐
17 | Loop Check Completed | Simulate and verify signal at DCS/PLC. Check polarity, scaling, and document results. | ☐
18 | Junction Box Connections Verified | Terminals matched with schedule. Gland entry correct. Shielded wires grounded as required. | ☐
19 | Instrument Support and Frame Quality | Use painted/galvanized/SS support. Proper height and aligned frame. Rust-free hardware. | ☐
20 | Environmental Compatibility Verified | Confirm Ex-d/Ex-ia rating, corrosion resistance, and operating limits for ambient condition. | ☐
21 | Process Line Cleaning Verified | Line flushed, debris removed, blow-through completed. Protect open ports until installation. | ☐
22 | Accessibility for Maintenance | Instruments must be accessible without scaffolding. Platform or ladder should be provided if needed. | ☐
23 | Instrument Zero Checked After Installation | Perform and log zero check post-mounting. Adjust offset if required. Ensure filled tubing. | ☐
24 | Conformance with Project Specification | Match all specs including thread, material, certification. Non-conformity to be flagged/documented. | ☐
25 | Photographic Documentation | Capture clear photos of tag, mounting, termination. Save with consistent naming in DMS. | ☐
Done by:
Verified by