## Interface Level Measurement Sel
Interface Level Measurement Selection Checklist
S.No | Checklist Item | Details to be Verified | ✔ | Remarks
1 | Process Fluid Types | Identify the two immiscible phases (e.g., oil-water, condensate-water, slurry-liquid). Confirm density difference is sufficient for measurement. | ☐
2 | Process Pressure Range | Verify minimum and maximum operating pressure. Ensure sensor can withstand normal and surge pressures. | ☐
3 | Process Temperature Range | Check minimum/maximum temperatures and any thermal cycling. Verify compatibility with instrument materials. | ☐
4 | Density of Each Phase | Record densities at operating conditions for calibration accuracy. Ensure difference ≥ recommended by manufacturer. | ☐
5 | Dielectric Constant (for RF/Capacitance) | Obtain dielectric values of both phases if using capacitance technology. | ☐
6 | Interface Layer Thickness | Confirm if interface is sharp or emulsion layer exists; choose technology accordingly (e.g., radar vs displacer). | ☐
7 | Vapour Space Conditions | Note vapour composition, pressure, and potential condensation for non-contact measurement types. | ☐
8 | Solids/Slurry Content | Check if solids or wax exist that may coat probes or block floats. | ☐
9 | Foaming Tendency | Identify any foam formation affecting signal reflection or buoyancy. | ☐
10 | Coating or Build-Up Potential | Assess if process material can cause coating on sensing surfaces; plan for purge/cleaning. | ☐
11 | Corrosiveness of Fluids | Select wetted materials compatible with both phases and vapour space. | ☐
12 | Tank/Vessel Geometry | Document dimensions, nozzle locations, and available instrument mounting points. | ☐
13 | Agitation or Turbulence | Check for mixers, pumps, or inflow streams that can cause level fluctuations. | ☐
14 | Measurement Range & Span | Confirm full-scale span covers both phases and required accuracy. | ☐
15 | Required Accuracy | Define acceptable error margin for interface level reading. | ☐
16 | Response Time Requirement | Determine if real-time interface change detection is critical (e.g., fast separation processes). | ☐
17 | Power Supply & Signal Output | Specify instrument power requirements and signal type (4-20 mA, HART, Modbus, etc.). | ☐
18 | Hazardous Area Classification | Check IEC/ATEX/NEC zoning and ensure appropriate explosion-proof or intrinsically safe design. | ☐
19 | Mounting Orientation | Verify vertical/horizontal mounting compatibility. | ☐
20 | Maintenance Accessibility | Ensure instrument location allows for calibration, removal, and cleaning. | ☐
21 | Process Isolation | Confirm provision of isolation valves or bypass for safe removal/servicing. | ☐
22 | Environmental Conditions | Consider ambient temperature, humidity, vibration, and exposure to chemicals. | ☐
23 | Control System Integration | Ensure compatibility with PLC/DCS input cards and communication protocols. | ☐
24 | Calibration Method | Define field or lab calibration procedure, considering density/temperature effects. | ☐
25 | Manufacturer Recommendations | Review and comply with vendor-specific installation and calibration guidelines. | ☐