## Excel Tool for Instrument Power
Excel Tool for Instrument Power Calculation
A | DATA | [6 empty] | F | TOTAL
| 1 | HEAT DETECTOR | = | 1.5 | WATTS |  |  |  | DATA
| 2 | SMOKE DETECTOR | = | 1.5 | WATTS |  |  |  | 1 | PCS PANEL |  |  | = | 1 | UNIT
| 3 | FLAME DETECTOR | = | 7 | WATTS |  |  |  | 2 | ESD & FGS PANEL |  |  | = | 1 | UNIT
| 4 | GAS DETECTOR | = | 5 | WATTS |  |  |  | 3 | ATG PANEL |  |  | = | 1 | UNIT
| 5 | BELL | = | 5 | WATTS |  |  |  | 4 | CCTV PANEL |  |  | = | 1 | UNIT
| 6 | STROBE LIGHT | = | 5 | WATTS |  |  |  | 5 | FA PANEL |  |  | = | 1 | UNIT
| 7 | SOUNDER AND FLASSER | = | 7 | WATTS |  |  |  | 6 | METERING PANEL |  |  | = | 1 | UNIT
| 8 | ON-OFF VALVE (SOLENOID) | = | 18 | WATTS |  |  |  | 7 | OWS |  |  | = | 6 | UNIT
| 9 | TRANSMITTER | = | 1 | WATTS |  |  |  | 8 | EWS |  |  | = | 1 | UNIT
| 10 | POSITIONER | = | 10 | WATTS |  |  |  | 9 | PRINTER |  |  | = | 3 | UNIT
| 11 | PTZ CCTV | = | 7 | WATTS |  |  |  | 10 | SERVER |  |  | = | 2 | UNIT
| 12 | FIX CCTV | = | 5 | WATTS
[9 empty] | 1 | PCS PANEL |  |  | = | 700 | WATTS
[9 empty] | 2 | ESD & FGS PANEL |  |  | = | 800 | WATTS
B | PCS | [7 empty] | 3 | ATG PANEL |  |  | = | 700 | WATTS
| 1 | TRANSMITTER | 27 | UNITS |  |  |  |  | 4 | FA PANEL |  |  | = | 700 | WATTS
| 2 | POSITIONER | 3 | UNITS |  |  |  |  | 5 | CCTV PANEL |  |  | = | 700 | WATTS
[9 empty] | 6 | METERING PANEL |  |  | = | 700 | WATTS
[9 empty] | 7 | OWS |  |  | = | 300 | WATTS
CALCULATION | [8 empty] | 8 | EWS |  |  | = | 300 | WATTS
| 1 | TRANSMITTER | 27x 1 |  | = | 27 | WATTS |  | 9 | PRINTER |  |  | = | 100 | WATTS
| 2 | POSITIONER | 3 x 10 |  | = | 30 | WATTS |  | 10 | SERVER |  |  | = | 300 | WATTS
|  | TOTAL |  |  | = | 57 | WATTS |  | 11 | ATG SERVO TYPE |  |  | = | 20 | WATTS
[9 empty] | 12 | ATG LOCAL DISPLAY |  |  | = | 10 | WATTS
C | FGS | [7 empty] | 13 | ATG LOCAL DISPLAY |  |  | = | 10 | WATTS
| 1 | HEAT DETECTOR | 7 | UNITS | [5 empty] | LEVEL SWITCH CAPASITANCE TYPE |  |  | = | 2 | WATTS
| 2 | SMOKE DETECTOR | 19 | UNITS | [5 empty] | SPILL OIL DETECTOR |  |  | = | 5 | WATTS
| 3 | FLAME DETECTOR | 4 | UNITS
| 4 | GAS DETECTOR | 6 | UNITS
| 5 | BELL | 6 | UNITS |  |  |  | CALCULATION
| 6 | STROBE LIGHT | 1 | UNITS |  |  |  |  | 1 | PCS PANEL |  |  | = | 700 | x 1 | = | 700 | WATTS
| 7 | SOUNDER AND FLASSER | 2 | UNITS |  |  |  |  | 2 | ESD & FGS PANEL |  |  | = | 800 | x 1 | = | 800 | WATTS
[9 empty] | 3 | ATG PANEL |  |  | = | 700 | x 1 | = | 700 | WATTS
[9 empty] | 4 | FA PANEL |  |  | = | 700 | x 1 | = | 700 | WATTS
CALCULATION | [8 empty] | 5 | CCTV PANEL |  |  | = | 700 | x 1 | = | 700 | WATTS
| 1 | HEAT DETECTOR | 7 x 2 |  | = | 14 | WATTS |  | 6 | METERING PANEL |  |  | = | 700 | x 1 | = | 700 | WATTS
| 2 | SMOKE DETECTOR | 19 x 2 |  | = | 38 | WATTS |  | 7 | OWS |  |  | = | 300 | x 6 | = | 1800 | WATTS
| 3 | FLAME DETECTOR | 4 x 5 |  | = | 20 | WATTS |  | 8 | EWS |  |  | = | 300 | x 1 | = | 300 | WATTS
| 4 | GAS DETECTOR | 6 x 5 |  | = | 30 | WATTS |  | 9 | PRINTER |  |  | = | 100 | x 3 | = | 300 | WATTS
|  | TOTAL |  |  | = | 102 | WATTS |  | 10 | SERVER |  |  | = | 300 | x 2 | = | 600 | WATTS
[9 empty] | 11 | ATG SERVO TYPE |  |  | = | 20 | x 1 | = | 20 | WATTS
[9 empty] | 12 | ATG LOCAL DISPLAY |  |  | = | 10 | x 1 | = | 10 | WATTS
D | ESD | [7 empty] | 13 | LEVEL SWITCH CAPASITANCE TYPE |  |  | = | 2 x 2 |  | = | 4 | WATTS
[9 empty] | 14 | SPILL OIL DETECTOR |  |  | = | 5 x 2 |  | = | 10 | WATTS
| 1 | SOLENOID | 2 | UNITS | [5 empty] | TOTAL | [5 empty] | = | 7344 | WATTS
[10 empty] | PLUS (+) 25 % ERROR INFORMATION | [5 empty] | = | 9180 | WATTS
CALCULATION
| 1 | SOLENOID | 2x18 |  | = | 36 | WATTS
|  | TOTAL |  |  | = | 36 | WATTS | G | TOTAL 24 VDC
[10 empty] | PCS | = | 57 | WATTS
[10 empty] | FGS | = | 102 | WATTS
E | CCTV SYSTEM | [8 empty] | ESD | = | 36 | WATTS
| 1 | PTZ CCTV | 9 | UNITS | [5 empty] | CCTV | = | 73 | WATTS
| 2 | FIX CCTV | 2 | UNITS
CALCULATION
CALCULATION | [9 empty] | PCS |  |  | = | 57 | WATTS
| 1 | PTZ CCTV | 9 x 7 |  | = | 63 | WATTS |  |  | ESD |  |  | = | 102 | WATTS
| 2 | FIX CCTV | 2 x 5 |  | = | 10 | WATTS |  |  | FGS |  |  | = | 36 | WATTS
|  | TOTAL |  |  | = | 73 | WATTS |  |  | CCTV |  |  | = | 73 | WATTS
[10 empty] | TOTAL |  |  | = | 211 | WATTS
[10 empty] | PLUS (+) 50 % ERROR INFORMATION | [6 empty] | 316.5 | WATTS
EXTERNAL POWER FROM MCC
[9 empty] | MOV | [6 empty] | 400 VAC, 50 Hz, 3 phase. |  |  | 6EA