## Instrumentation Cable Terminati
Instrumentation Cable Termination Checklist
S.No | Section | Checklist Item | Reference Standard | Inspector Check (✔) | Remarks
1 | Preparation | Verify cable routing and identification as per the cable schedule. | Cable Schedule
|  | Check loop drawings, termination drawings, and P&IDs before work. | Loop Diagram
|  | Confirm cable gland type and size according to selection table. | Cable Gland Table
|  | Ensure sufficient cable length without unnecessary looping. | Cable Schedule
|  | Confirm firestop materials installed if crossing fire-rated barriers. | Installation Practice
2 | Cable Stripping | Strip outer sheath without damaging conductor insulation. | IEC 60228
|  | Maintain outer jacket up to 3–4 inches from termination point. | IEC 60092
|  | Insulate drain wires/shield ends using heat shrink sleeves. | IEC 60092
3 | Lugging & Crimping | Use compression lugs for stranded conductors. | IEC 61238
|  | Select correct die size as per cable core size. | IEC 61238
|  | Inspect joints for mechanical tightness & continuity. | IEC 61238
|  | Apply color-coded heat shrink sleeves on lugs. | IEC 61238
4 | Termination | Connect wires only to screw-type terminal blocks. | IEC 60947
|  | Follow polarity and shielding per vendor instructions. | IEC 60947
|  | Spare pairs terminated and identified as 'Spare'. | IEC 60947
5 | Inspection & Testing | Visually check neatness, bend radius, and shielding. | IEC 61557
|  | Perform continuity & insulation resistance tests. | IEC 61557
|  | Verify cable tags, labeling, and documentation. | IEC 61557
6 | Field Instruments | Terminate directly to field instrument terminal blocks. | IEC 60079
|  | Drain wires insulated and treated per grounding scheme. | IEC 60079
7 | Junction Boxes | Cable entries from bottom only to prevent moisture ingress. | IEC 60079
|  | Spare pairs terminated and labeled inside JB. | IEC 60079
8 | Grounding & Shielding | Follow single-point grounding philosophy. | IEC 60947
|  | No daisy-chaining or floating shields allowed. | IEC 60947
9 | Foundation Fieldbus | Maintain polarity (Black +, White –, Shield). | IEC 61158 / SAES-J-902
|  | Install terminators at two ends only. | IEC 61158
10 | Intrinsically Safe | Terminate IS cables in dedicated IS cabinets. | IEC 60079-14
|  | Maintain min. 50 mm separation from non-IS cables. | IEC 60079-14
|  | Verify ATEX/IECEx certificates of IS barriers. | IEC 60079-14
11 | Fire Alarm & ESD | Use red cables for Fire Alarm, orange/yellow for ESD. | NEC 760 / NFPA 72
|  | Perform end-to-end loop test with supervisory current. | NEC 760 / NFPA 72
12 | Inside Panels | Terminate conductors adjacent on same strip. | IEC 60204-1
|  | No coiling; cut cables to exact required length. | IEC 60204-1
13 | Tagging & Labelling | Install SS316 tags for outdoor cables. | IEC 60445
|  | Use heat shrink sleeves only, no adhesive labels. | IEC 60445
14 | Quality Control | Update as-built termination drawings after inspection. | Project QA/QC
|  | Document Megger test results in Pre-Commissioning dossier. | IEC 61557
15 | Safety Precautions | Confirm isolation & apply lockout-tagout before work. | OSHA 1910.147 / IEC 60204-1
|  | Follow PPE requirements: helmet, gloves, arc-rated clothing. | NFPA 70E / OSHA
|  | Use gas detectors in confined/hazardous areas. | IEC 60079-29