## Thermowell Selection Checklist
Thermowell Selection Checklist for EPC Engineers
Step / Parameter | What to Specify | Options / Guidelines | Engineering Notes
1. Process Connection Type & Size | Define how thermowell attaches to process | Threaded (NPT) Flanged (ANSI/DIN) Weld In Socket Weld Sanitary Clamp | Match piping class and flange face type (150# 300# flat raised ring joint). Welded types are permanent and leak proof.
2. Insertion Length (U) | Depth from process connection to tip | Standard lengths 2.5″ 4.5″ 7.5″ 10.5″ 13.5″ 16.5″ 22.5″ | Pipelines reach pipe centerline (≥1/3 diameter). Vessels typically 6–12″. Too short inaccurate. Too long vibration risk.
3. Lagging Extension (T) | Extra length for insulation clearance | 2″ 3″ or custom | Ensures sensor head projects beyond jackets insulation for access.
4. Extension Length (E) | Distance from process connection to instrument head | 3″ 6″ (standard) | Keeps head/electrical housing away from hot surfaces. Improves maintenance safety.
5. Sensor Length (X) | Length of probe to match thermowell bore | Threaded/Socket Weld X = U + T + E + 1.5″ Flanged X = U + T + E + 2.0″ | Probe must touch bore tip for accuracy. Example U=7.5″ T=3″ E=0 → X=12″.
6. Bore Diameter (B) | Internal hole size for probe | 0.260″ → ¼″ RTD or TC probe 0.385″ → ⅜″ thermometer bulb | Clearance must be minimal to reduce thermal lag but sufficient for probe insertion removal.
7. Shank Style | Geometry of immersion portion | Straight Stepped Tapered Built up | Straight = general purpose. Stepped = faster response lower strength. Tapered = best for high velocity vibration.
8. Material of Construction | Based on corrosion, temperature, pressure | Carbon Steel SS304 SS316 SS316L Monel Hastelloy Titanium Tantalum PTFE lined | Always check corrosion resistance charts. SS316 is most widely used for chemical service.
9. Flow Induced Vibration Check | Verify against ASME PTC 19.3 TW 2016 | Ensure natural frequency > vortex shedding frequency | Critical for high velocity steam gas or liquid service. Use tapered wells when in doubt.
10. Thermal Response | Minimize measurement lag | Use thinner tips Use stepped/tapered wells Ensure probe contact | Air gaps act as insulators → apply thermal grease or use spring loaded probes.
11. Pressure Rating | Match piping flange rating | ANSI 150# 300# 600# 1500# 2500# | Must withstand process design pressure. Confirm flange face type (raised flat RJ).
12. Probe Fit & Heat Transfer | Ensure good contact | Spring loaded probes Thermal grease | Avoid excessive annular clearance to improve accuracy and response.