## Radar Calculator
RADAR LEVEL TRANSMITTER CALCULATOR
4–20 mA Output Calculation for Tank Level Measurement
📋 INSTRUMENT DATA
Tag Number: | XXXXXXX | Date: | 2025-09-29
Tank ID: | XXXXX | Technician: | ABCD
🔧 INPUT PARAMETERS
Tank Height (H) | 6 | meters
Blocking Distance (BD) | 0.7 | meters
Water Level (L) | 3 | meters
📊 CALCULATED RESULTS
Effective Span | 5.3 | meters
Level Percentage | 56.6038 | %
Output Current | 13.0566 | mA
📈 VERIFICATION TABLE
Test Point | Water Level (m) | % Level | Expected mA
Empty (0%) | 0 | 0 | 4
Quarter (25%) | 1.325 | 25 | 8
Half (50%) | 2.65 | 50 | 12
Three-Quarter (75%) | 3.975 | 75 | 16
Full (100%) | 5.3 | 100 | 20
📝 FORMULAS USED
Effective Span = Tank Height (H) - Blocking Distance (BD)
Level % = (Water Level / Effective Span) × 100
Output mA = 4 + (Level % / 100 × 16)
© 2025 Radar Level Transmitter Calculator ¦ Industrial Use