## Sheet1
Control Valve Troubleshooting Checklist
Section | Step No. | Check Item | Action / Description | Expected Result
1. Safety & Work Preparation | 1.1 | Work Permit & Authorization | Confirm valid LOTO / Work Permit is obtained and control room informed. | Permit approved and communication done
| 1.2 | Process Isolation | Verify valve is bypassed or process line isolated (upstream/downstream valves closed). | Valve safely isolated
| 1.3 | Depressurization | Ensure section is depressurized, drained, and cooled to safe temperature. | No pressure or temperature hazard
| 1.4 | Energy Source Isolation | Lock out instrument air, electrical and hydraulic supplies; tag isolation points. | All energy sources locked out
| 1.5 | PPE & Area Safety | Confirm PPE usage and area safety conditions. | Safe working area
2. Signal Verification | 2.1 | Controller Output Check | Verify DCS/PLC output corresponds to control command. | Matches setpoint range
| 2.2 | Loop Signal at Valve Positioner | Measure 4–20 mA using DMM or loop calibrator. | Signal within expected range
| 2.3 | HART/Smart Positioner Data | Use communicator to compare SP vs PV. | SP ≈ PV; no faults
| 2.4 | I/P Converter Output | Measure pneumatic output (3–15 psi) for current signal. | Linear correspondence
| 2.5 | Cabling & Terminals | Inspect for corrosion, moisture, or loose wires. | Clean and tight connections
3. Air Supply & Actuator Health | 3.1 | Air Pressure at Actuator Inlet | Measure supply pressure using test gauge. | Within datasheet range
| 3.2 | Air Stability Check | Observe pressure stability during operation. | Stable pressure
| 3.3 | Air Quality | Check regulator bowl for moisture/oil; inspect filters. | Clean and dry air
| 3.4 | Air Leak Detection | Use leak detection spray or listen for leaks. | No leaks detected
| 3.5 | Manual Stroke Test | Apply controlled air and observe valve travel. | Smooth full stroke
4. Actuator Isolation & Mechanical Test | 4.1 | System Isolation Confirmed | Verify LOTO and isolation active. | Safe for work
| 4.2 | Actuator–Valve Disconnection | Disconnect linkage safely. | Mechanical parts free
| 4.3 | Independent Actuator Stroke | Apply test air or jog motor. | Full smooth motion
| 4.4 | Feedback Linkage Check | Inspect linkage or lever for binding. | No mechanical obstruction
5. Valve Body Check | 5.1 | Manual Operation Test | Operate valve manually using handwheel or override. | Smooth movement
| 5.2 | Stem Packing Inspection | Slightly loosen gland nuts to check friction. | Stem moves freely
| 5.3 | Stem Leakage Check | Apply soap solution to packing area. | No bubbles or leakage
| 5.4 | Partial Stroke Test (PST) | Perform PST for critical valves. | Response within limits
6. Post-Maintenance Validation | 6.1 | Positioner Calibration | Recalibrate and verify travel 0–100%. | Linear response
| 6.2 | Full Stroke Test | Command full range from DCS and observe. | Smooth full stroke
| 6.3 | Leak Test | Re-pressurize and check for leakage. | No leakage detected
| 6.4 | Documentation & Handover | Record findings, restore system, and inform control room. | System normalized