## PLC Running Inspection
DETAILED RUNNING INSPECTION CHECKLIST FOR PLC CONTROL PANELS
Section | Inspection Point | What to Check / Observe | Observation / Reading | Acceptable Condition | Measured Temperature / Humidity | LED / Visual Status | Deviation (Yes/No) | Action / Remarks / SAP Notification No.
General Visual & Safety Checks | Panel Identification | Verify tag number, nameplate, and area classification |  | Matches drawings and asset register
| Access and Housekeeping | Ensure area around panel is clean and dry |  | Minimum 1m clear space around panel
| Door Condition and Interlock | Check door hinges, latch, and interlock operation |  | Smooth movement, interlock intact
| Safety Signage | Check for voltage warning and grounding labels |  | Visible and undamaged
| Earthing Continuity | Visually confirm bonding and straps |  | Tight, no corrosion
| Deviation Check | Note any damage, missing label, or modification |  | None present
Power Supply & AC Function | Incoming AC Supply Indication | Check power ON lamps |  | All phases ON and balanced
| Voltage Level | Measure incoming terminal voltage |  | Within ±5% of rated value
| Power Supply Health (24VDC) | Check redundant power supply LEDs |  | Both healthy, no alarm
| Power Supply Temperature | Measure PSU casing temperature |  | <50°C typical
| UPS / SMPS Fan Noise | Listen for unusual sound or vibration |  | Smooth and quiet
| Any Sign of Heating or Smell | Inspect insulation or odor |  | No discoloration or smell
PLC CPU & I/O Modules | CPU Module LEDs | Observe RUN/ERROR/COMM LEDs |  | RUN steady ON, ERROR OFF, COMM flashing
| Diagnostic Modules | Check health/fault/communication LEDs |  | Health green, Fault OFF
| I/O Module LEDs | Verify input/output status vs process |  | Logical ON/OFF as per process
| Redundancy Modules | Observe Active/Standby LED |  | One active at a time
| Module Temperature | Measure using IR thermometer |  | ≤45°C typical
| Module Mounting | Check for alignment and vibration |  | Firmly mounted
| Deviation Check | Any blinking fault LED or hot spot |  | None acceptable
Communication & Networking | Ethernet / Network Links | Observe link/activity LEDs on switches |  | Steady link, active blink
| Redundant Communication | Check PRP/RSTP switchover |  | Switchover successful
| Profibus/Fieldbus Connectors | Inspect LED and connection tightness |  | No bus fault
| Communication Temperature | Check with IR thermometer |  | Below 45°C
| Network Cable Routing | Ensure segregation from power cables |  | ≥100mm separation
| Deviation | Loose connectors or off LED |  | None
Environmental & Cooling | Ventilation Fans | Check airflow and noise |  | Continuous, no abnormal noise
| Air Filters | Inspect inlet/outlet filters |  | Free from dust
| Panel Heater (if applicable) | Verify operation under cold condition |  | ON below 15°C
| Panel Internal AC | Check cooling and drainage |  | Proper cooling, drain clear
| Panel Internal Temperature | Measure using IR thermometer |  | 30–40°C typical
| Humidity Level | Check hygrometer or condensation |  | <60% RH, no moisture
| Deviation | Heat/fan/moisture abnormalities |  | None
Wiring & Cable Arrangement | Wiring Arrangement | Inspect cable routing |  | Neat and separated
| Trunking and Ducts | Check covers and overcrowding |  | Covers closed, no loose wires
| Cable Ties and Dressing | Check strain and spacing |  | Proper spacing, no tension
| Cable Glands | Verify tightening and sealing |  | Intact and dust-proof
| Ferrules and Labels | Check for readability |  | All tags legible
| Deviation | Any non-standard routing or missing cover |  | None
Auxiliary Components | Panel Lights | Toggle and check lamp operation |  | Functional, correct color
| Pushbuttons | Check physical condition |  | No cracks or sticking
| Alarm Buzzer | Check logic-based activation |  | Active as per alarm condition
| Door Limit Switch | Verify on HMI or PLC input |  | Changes state on door open
| Internal 230V Socket | Inspect condition (no use) |  | Intact and covered
Documentation & Reporting | Cross-check As-Built Drawing | Match wiring and I/O mapping |  | Updated and accurate
| Record Temperature Readings | Document PSU and module temperature |  | Within limits
| Record Humidity Level | Note hygrometer readings |  | <60% RH
| Record LED Snapshot | Take photos/log of modules |  | Used for trending
| Deviation Management | Log all abnormal findings |  | Create SAP Notification
| Follow-up Plan | Schedule corrections in next shutdown |  | Planned and documented