## Detailed EMFM ITP
Electromagnetic Flow Meter Inspection and Test Plan (ITP)
Sr No | Activity | Inspection Stage | Method / Procedure | Acceptance Criteria | Responsible Party (Vendor / EPC / Client) | Record / Format
1 | Incoming Material Verification | Hold | Visual inspection, MTC review, Datasheet comparison | Material grade, size, rating match PO & EN10204 | Vendor / EPC QAQC / Client | MTC, IR
2 | Flow Tube Body Inspection | Witness | Check welding, coating, flange rating, corrosion protection | No cracks, uniform weld, correct rating, coating defect-free | Vendor / EPC | IR
3 | Liner Material Verification | Witness | Visual inspection, OEM reference, surface check | Correct liner (PTFE/PFA/Rubber), no blisters/pinholes | Vendor / EPC | IR
4 | Electrode Material Verification | Witness | Visual inspection, material verification | Material matches datasheet (SS316L/Tantalum/Titanium) | Vendor / EPC | IR
5 | Coil Resistance Test | Witness | Multimeter test on excitation coil | Resistance within OEM-specified limits | Vendor / EPC | Test Report
6 | Nameplate & Tag Verification | Review | Model, serial number, tag number verification | Matches approved datasheet & instrument index | EPC / Client | IR
7 | Dimensional Verification | Witness | Measurement using Vernier/Micrometer | Face-to-face, flange OD/ID within tolerances | Vendor / EPC | IR
8 | Hydrostatic Pressure Test (If Required) | Witness | Hydro test at 1.5x design pressure | No leaks, no deformation, pressure holds | Vendor / Third Party | Hydro Test Certificate
9 | Insulation Resistance Test | Witness | Megger test at 500–1000V | IR ≥ 100 MΩ or OEM specification | Vendor | Test Sheet
10 | Excitation Coil Verification | Hold | OEM procedure - Coil current/voltage check | Values within OEM tolerances | Vendor / Client | FAT Report
11 | Electrode Continuity Test | Witness | Resistance measurement across electrodes | Continuity within OEM limit, no open circuit | Vendor | FAT Report
12 | Terminal Box & Cable Gland Inspection | Witness | Physical inspection, cable gland verification | Tight connections, proper IP rating, correct gland type | Vendor / EPC | FAT Checklist
13 | Internal Wiring Verification | Witness | Check wiring routing, labels, termination | Neat wiring, correct terminals, no loose connections | Vendor / EPC | IR
14 | Flow Rig Calibration (Performance Test) | Hold | Multiple-point calibration on certified flow rig | Accuracy ±0.2%–0.5%, linearity, repeatability OK | Vendor / Client | Calibration Certificate
15 | Zero Flow Stability Check | Witness | Run test with no flow | Zero within OEM tolerance, no drift | Vendor / EPC | FAT Report
16 | Pulse Output Verification | Witness | Simulate and validate pulse frequency | Pulse count matches K-factor configuration | Vendor / EPC | FAT Report
17 | 4–20 mA Output Test | Witness | Simulate 0%, 50%, 100% flow | Output within ±0.05–0.1% accuracy | Vendor / EPC / Client | Loop Test Sheet
18 | HART/Modbus/Profibus Communication Test | Witness | Digital communication check to DCS/PLC | Correct PV, diagnostics, configuration | Vendor / EPC | Protocol Test Report
19 | Site Installation Inspection | Witness | Orientation, earthing, flange bonding, straight-run check | Meets OEM installation requirements | EPC / Client | SIT Report
20 | Cable Shielding & Segregation Check | Witness | Inspect routing and shielding | Signal cable segregated, grounded one side only | EPC | SIT Checklist
21 | Pre-Commissioning Checks | Witness | Power-up, diagnostics, empty pipe test | Stable operation, no error codes | EPC / Client | Pre-commissioning Report
22 | Commissioning & Loop Test | Hold | Loop test, alarm checks, interlock verification | Signals accurate, loops functional | EPC / Client | Commissioning Report
23 | Final Documentation Review | Review | MDR/As-built/QCP/Certificates check | All documents complete & approved | EPC / Client | MDR / Dossier