## Fieldbus Checklist
Detailed Foundation Fieldbus Installation Checklist
Category | Inspection Item | Detailed Description / Acceptance Criteria | Reference Standard | Responsible Party | Remarks / Corrective Action | Verified By | Date | Status (OK / Not OK / NA)
Design & Documentation | Verify FF segment design | Ensure segment design includes trunk length, spur count, terminators, and voltage drop calculations | IEC 61158 / FF-816 | Engineering
| Confirm power conditioner sizing | Verify load current and redundancy of FF power supply modules | FF-830 / ISA SP50.02 | Engineering
| Check device interoperability list | All field devices, host systems, and couplers should be FF-registered | FF-816 / FF-830 | Engineering
| Review hazardous area classification drawings | Ensure all devices and junction boxes are suitable for designated zones | IEC 60079-10 / IEC 60079-14 | Engineering
| Verify earthing and shielding scheme | Single-point shield grounding defined at control room side | IEC 61158 / ISA SP50.02 | Engineering
Cable Selection | Use approved FF Type A cable | 18 AWG twisted pair, 100Ω impedance, <100pF/m capacitance, overall shield | IEC 61158 / FF-816 | Procurement
| Check cable certification for Ex areas | Cables shall be certified for IEC 60079-14 installation | IEC 60079-14 | Procurement
| Verify cable drum labeling | Ensure manufacturer, type, length, and test certificate available | Project Spec / FF-816 | Procurement
Cable Laying | Segregate FF cables from power | Maintain 300 mm clearance from 230/440V power cables | IEC 60364 / FF-816 | Contractor
| Maintain bend radius | ≥10 × outer diameter; avoid mechanical stress or crushing | IEC 61158 | Contractor
| Ensure continuous runs without joints | Avoid mid-run joints unless approved junction boxes used | ISA SP50.02 | Contractor
| Verify tray bonding and continuity | All trays properly bonded and earthed | IEC 60079-14 | Contractor
| Install cable identification sleeves | Heat-shrink sleeves near both terminations | FF-830 | Contractor
Shielding | Maintain shield continuity | Ensure shield foil and drain wire continuous from end to end | IEC 61158 | Contractor
| Isolate shield at device end | Connect shield only at control room or power conditioner end | ISA SP50.02 / IEC 61158 | Contractor
| Check shield bonding at JB | Spur and trunk shields shall be isolated within IS junction boxes | IEC 60079-14 | Contractor
Earthing | Ensure single-point grounding | Ground shield only at marshalling/power conditioner end | IEC 61158 / ISA SP50.02 | Contractor
| Bond metallic JB enclosures | Bond with 4 mm² min copper wire to plant earth grid | IEC 60079-14 | Contractor
| Inspect earth continuity | Resistance ≤ 1 ohm between equipment and main grid | IEC 60079-17 | Inspector
Junction Box | Use certified Ex e / Ex d enclosures | Verify approval markings (ATEX/IECEx) for hazardous zones | IEC 60079-0 / IEC 60079-7 | Procurement
| Install approved glands | Metallic, Ex-rated glands sized per cable OD | IEC 60079-14 | Contractor
| Verify internal wiring | Proper segregation of trunk and spur, ferruled terminations | ISA SP50.02 | Contractor
| Check ingress protection rating | Minimum IP66 for outdoor installation | IEC 60529 | Inspector
Device Wiring | Confirm polarity at transmitter | Orange (+), Blue (–) | FF-830 | Contractor
| Use approved IS barriers where applicable | Check entity parameters and loop approval | IEC 60079-11 / IEC 60079-25 | Contractor
| Crimp terminals properly | No loose strands, use insulated ferrules | ISA SP50.02 | Contractor
| Ensure spur length compliance | Each spur ≤ 120 m, total segment ≤ 1900 m | FF-816 | Engineering
Termination | Install exactly two terminators | One at power conditioner, one at far end of segment | FF-816 / IEC 61158 | Contractor
| Verify termination resistance | Each terminator = 100Ω ±1%, parallel = 50Ω | FF-830 | Inspector
Power Conditioner | Verify redundancy configuration | Primary and backup modules in hot standby | FF-830 / Project Spec | Engineering
| Measure output voltage | 22–32 VDC nominal under load | IEC 61158 | Inspector
Barrier | Check output entity parameters | Ensure barrier Uo, Io, Po < device Ui, Ii, Pi | IEC 60079-11 | Inspector
Testing | Check bus voltage at each spur | ≥11 VDC at device under load | FF-816 | Commissioning
| Verify segment live list | All devices visible in host DCS system | FF-830 | Commissioning
| Record signal quality index (SQI) | SQI ≥ 3.5 and jitter ≤ 2 µs | FF-816 | Commissioning
| Check segment noise levels | LF noise < 50 mV, HF noise < 100 mV | FF-816 | Commissioning
| Check terminator presence | Use FF test tool or oscilloscope | ISA SP50.02 | Commissioning
Inspection | Inspect cable glands and seals | Ensure no unused openings, glands tightened | IEC 60079-14 | Inspector
| Verify labels and tagging | All JB, devices, and cables labeled per drawings | FF-830 | Inspector
| Inspect cable continuity | No open or short circuit, verify with multimeter | ISA SP50.02 | Inspector
| Verify earthing and bonding | Test all metallic connections continuity < 1 ohm | IEC 60079-17 | Inspector
Documentation | Maintain segment report | Record all devices, voltages, terminators, and test values | FF-830 | Commissioning
| Attach vendor certificates | Include cable test report, Ex certificate, device datasheet | IEC 60079 / FF-816 | QC
| Mark-up as-built drawings | Include JB tag, segment ID, cable number, terminator location | Project Spec | QC
| Record loop test results | Include pass/fail criteria and calibration records | ISA SP50.02 | QC

## Legend_Standards
Standard / Code | Description
IEC 61158 | Industrial communication networks – Fieldbus specifications
FF-816 | Foundation Fieldbus Physical Layer – Cable and wiring requirements
FF-830 | Foundation Fieldbus Installation Guidelines
ISA SP50.02 | Fieldbus Standard for Use in Industrial Control Systems
IEC 60079-14 | Explosive Atmospheres – Electrical Installations Design, Selection and Erection
IEC 60079-17 | Explosive Atmospheres – Inspection and Maintenance of Electrical Installations
IEC 60079-11 | Intrinsic Safety – Equipment Protection by Intrinsic Safety 'i'
IEC 60079-25 | Intrinsically Safe Electrical Systems – Design and Verification