## Field Instrument Maintenance
Advanced Integrated Field Instrument Reliability & Cyber-Secure Maintenance Checklist
Category | Sub‑Category | Detailed Checklist Item | Expected Standard | Status | Remarks
Instrument Health | Diagnostics | Review NE107 health status | No active red/yellow alarms
|  | Check device alert logs for recurring faults | No repeated alerts
| Calibration | Verify calibration drift (as‑found vs as‑left) | < 0.1% deviation or OEM limit
| Sensor Condition | Inspect diaphragm, antenna, RTD wiring | No corrosion, wear, or coating
| Configuration | Verify scaling, linearization, damping | Matches datasheet/process requirement
Communication | HART/FF/APL | Check communication integrity and polling | <1% packet error
| Network Layer | Verify shielding and grounding quality | Properly bonded/terminated
|  | Check CRC errors on switches | Zero or minimal
| Wireless | Check RSSI, mesh routing, retries | RSSI > -75 dBm
| Mapping | Verify OPC-UA/Modbus tag mapping | 100% tag accuracy
Control Valves | Positioners | Analyze valve signature curve | No abnormal hysteresis
|  | Check friction & stiction levels | Within OEM friction index
| Actuator | Inspect air supply pressure & quality | Dry and regulated air
| Mechanics | Check linkage integrity & wear | Smooth movement
| Safety | Verify fail-safe action | Operates correctly
Power/Environment | Power | Verify loop power supply stability | 24V ±5%
| Cabling | Inspect cable tray, insulation, sheathing | No cuts, moisture, rodent damage
| Enclosure | Check IP rating & sealing | No ingress or cracks
| Ex-Proof | Verify gland tightening & earthing | Meets Ex compliance
| Environmental | Check condensation & humidity | <60% internal humidity
Cybersecurity | Firmware | Check firmware authenticity & hash | Matches OEM signature
| Access Control | Verify password policy & RBAC | Strong password enabled
| Network | Identify unused open ports/services | All unused ports closed
| Logs | Inspect audit logs for unauthorized access | No suspicious events
| Patching | Confirm latest OEM security patches applied | Up-to-date
Documentation | Records | Update CMMS/EAM with maintenance entries | Complete with time stamp
| SIL | Verify proof-test records and validity | Within test interval
| Backup | Validate configuration backups & checksum | Checksum match
| Reports | Upload FMEA, incident logs | All documents updated
| Compliance | Check IEC 61511 & 62443 compliance | No gaps
IIoT/Digital Twin | Data Sync | Verify cloud/edge sync of device data | No missing data
| Analytics | Check predictive alarms & trends | Reviewed and validated
| Twin Accuracy | Compare digital twin vs real readings | <2% deviation
| AI Thresholds | Validate anomaly detection thresholds | Aligned with process
| Historian | Verify historian tag updates | Continuous logging
Shutdown/Startup | SIL Loops | Confirm safe-state operation | Valve in correct fail state
| Interlocks | Verify permissives & interlocks | All active as designed
| Hot Cutover | Check redundancy & switchover | No packet loss
| Bypass | Review bypass activation logs | No unauthorized bypass
| Authorization | Confirm all tasks documented & approved | Complete