## Valve Characteristic Checklist
Control Valve Characteristic Selection Checklist
Checklist Category | Detailed Checklist Item | Status | Remarks
Control Objective | Define if the loop controls flow, temperature, pressure, or level
Identify required response time and tuning sensitivity for the loop
System DP Evaluation | Review pump and compressor curves for differential pressure variability
Evaluate friction losses across full flow range using piping isometrics
Fluid Characteristics | Determine if the fluid is compressible (steam/gas) or incompressible (liquid)
Check if the fluid undergoes flashing, cavitation, or expansion
Valve Authority | Calculate valve authority at minimum, normal, and maximum load
Assess if low authority requires equal percentage characteristic
Rangeability | Identify minimum controllable flow requirements
Evaluate turndown ratio required for stable control
Installation Curve | Compute Kvr at multiple flow conditions
Overlay installed curve with inherent linear and equal percentage curves
Mechanical Considerations | Check seat wear, erosion risk, and throttling zone stress
Verify actuator thrust, torque, and air supply adequacy
Positioner & Accuracy | Confirm positioner resolution for required stroke range
Check if advanced positioners (SMART / Digital) are needed
Energy Efficiency | Evaluate pump throttling losses and steam consumption impacts
Confirm correct characteristic minimizes unnecessary energy waste
Safety & SIL | Confirm suitability for SIS loops and safe failure behavior
Ensure characteristic supports required reliability (EP preferred for SIS modulating)
Final Selection | Finalize chosen characteristic: Linear, Equal Percentage, Quick Opening
Document justification based on hydraulic and control analysis