## Sheet1
Control Valve Site Acceptance Test (SAT) Checklist for EPC Engineering
Section | Step No | Task | ExpectedResult | ToolsRequired | AcceptanceCriteria | Remarks | CheckedBy | Date | Pass/Fail | Measured/Value
Preparatory Activities | 1.1 | Locate valve datasheet, actuator & positioner manuals, hook-up drawings, loop diagram, and P&ID | All documents available on site and match tag | Files/Tablet | All documents present and match tag number
| 1.2 | Verify nameplate: tag number, valve type, size, pressure class, trim, flow direction, rated temp | Nameplate matches datasheet | Visual inspection, datasheet | Nameplate exactly matches datasheet values
| 1.3 | Obtain LOTO, work permits, and notify control room of planned tests | Permits signed and communications logged | Permit paperwork, radio/phone | LOTO and permits attached to test pack; ops notified
| 1.4 | Ensure piping supports and alignment complete | No temporary supports causing misalignment | Wrench, visual | Supports complete; no misalignment observed
| 1.5 | Ensure instrument air and electrical power availability and isolation points known | Air & power available and isolation points documented | Pressure gauge, multimeter | Air header pressure available; electrical isolations confirmed
| 1.6 | Assemble calibrated tools and check calibration dates | All tools available and in calibration | Loop calibrator, pressure gauge, multimeter, HART | Calibration certificates attached and dates valid
| 1.7 | Confirm PPE, rescue and first-aid contacts | Team equipped with required PPE | PPE kit | PPE present and team briefed
Visual & Mechanical Inspection | 2.1 | Nameplate & tag verification against datasheet | Tag and nameplate correct | Datasheet, pen/camera | Tag matches datasheet; photograph attached
| 2.2 | Verify flow direction arrow orientation | Flow arrow aligns with piping | Visual, camera | Arrow orientation correct
| 2.3 | Inspect body, bonnet, flanges for damage | No transport damage, dents, cracks | Flashlight, camera | No visible damage; if found log NCR
| 2.4 | Verify gaskets and flange bolt presence & torque | Gaskets present; bolts torqued to spec | Torque wrench | Torque values per vendor; record torque
| 2.5 | Confirm actuator type & mounting orientation | Actuator matches drawing; mounting secure | Wrench, torque wrench | Actuator type and orientation correct
| 2.6 | Verify yoke, coupling, and mounting bolts torque | Bolts torqued and coupling aligned | Torque wrench, feeler gauge | Torque per spec; no lateral force
| 2.7 | Check accessory placement (positioner, FRL, solenoids) | Accessories fitted and accessible | Visual, camera | Accessories present and tubing neat
| 2.8 | Inspect packing/gland & check gland nut seating | Packing not damaged; gland nuts even | Visual, spanner | Packing acceptable; no visible leaks
| 2.9 | Manual mechanical freedom check (actuator depressurized) | Manual override moves smoothly | Manual crank, visual | Smooth movement without binding
Instrument Air Verification | 3.1 | Measure FRL filter-regulator pressure | Pressure set to vendor recommended (typ 4-6 bar) | Calibrated pressure gauge | Pressure within vendor range
| 3.2 | Confirm FRL bowl free of moisture and drain if required | No water in bowl or drained | Visual, drain tool | No moisture present
| 3.3 | Inspect tubing for kinks, correct size and slope | Tubing correct and supported | Visual, tape measure | Tubing material and routing per drawing
| 3.4 | Tighten fittings and clamp supports | No loose fittings or supports | Wrenches | All fittings secure
| 3.5 | Pressurize actuator & positioner ports; leak test with soap solution | No bubbles at fittings/joints | Soap solution, pressure gauge | No leaks; if present, repair and recheck
| 3.6 | Air stability test: cycle valve slowly and monitor inlet pressure | No significant pressure drop during cycling | Stopwatch, pressure gauge | Pressure drop within acceptable limit; record values
| 3.7 | Operate solenoid valves manually to confirm switching and exhaust routing | Solenoids switch and exhaust correctly | Hand tool, visual | Solenoid action correct
Electrical & Signal Wiring Verification | 4.1 | Verify cable type, gland seals and terminal torque | Correct cable, glands sealed and terminals torqued | Multimeter, torque wrench | Cables and terminations per spec
| 4.2 | Confirm earthing/grounding continuity | Ground continuity to earth | Multimeter | Earth resistance within acceptable limits
| 4.3 | Identify IO channel and compare wiring to loop diagram | Wiring matches loop diagram | Loop diagram, marker | Wiring matches diagram
| 4.4 | Check 4-20 mA loop continuity and polarity with calibrator/multimeter | Loop continuous and correct polarity | Loop calibrator, multimeter | Polarity correct; continuity confirmed
| 4.5 | Measure loop resistance and ensure within device capability | Loop resistance acceptable | Multimeter | Resistance less than device max; record ohms
| 4.6 | Verify supply voltage and phase sequence for electric actuators | Voltage and phase sequence correct | Multimeter, phase rotation meter | Voltage within tolerance; correct phase order
| 4.7 | Inspect motor protection settings | Motor protection devices set per spec | Manual, screwdriver | Protection settings confirmed
| 4.8 | Connect HART communicator and read diagnostics if smart device present | Device communicates and reports no critical errors | HART communicator | Tag, range and diagnostics readout attached
Mechanical Stroke & Freedom of Movement | 5.1 | Manual initial stroke with actuator depressurized | Valve moves full travel smoothly | Manual crank, visual | No binding or tight spots
| 5.2 | Full stroke under air/power: command full open and close | Smooth uniform travel and no abnormal noise | Loop calibrator, stopwatch, camera | Stroke completes fully and evenly
| 5.3 | Record stroke speed, noise, friction, asymmetry | Recordings available and within vendor limits | Stopwatch, notebook | Stroke time within spec; note anomalies
| 5.4 | Verify end-stop and travel adjustments | End stops match specified travel range | Feeler gauge, wrench | End stops set and not overconstrained
Actuator & Positioner Functional Testing | 6.1 | Set baseline zero/span (4 mA closed, 20 mA open or per spec) | Positioner scaled correctly | Loop calibrator, HART | Zero/span set and recorded
| 6.2 | Inject 4,8,12,16,20 mA and record valve position at each point | Position matches expected values at each point | Loop calibrator, position feedback | Positions within tolerance per spec
| 6.3 | Cycle signal up and down to check repeatability | Valve returns to same position for identical signals | Loop calibrator, notebook | Repeatability within specified % of span
| 6.4 | Deadband and hysteresis check around a point (±0.5 mA) | Minimal hysteresis/deadband | Loop calibrator | Deadband/hysteresis within project limits
| 6.5 | Measure full open→close and close→open times | Stroke times recorded and compared to spec | Stopwatch | Stroke times within vendor/project limits
| 6.6 | Positioner tuning: adjust gain/offset/damping to avoid hunting | Stable response with no hunting | HART communicator, screwdriver | Tuning parameters recorded and stable
| 6.7 | Capture smart diagnostics (supply pressure, valve effort, status) | Diagnostics logged | HART communicator | Diagnostic snapshot attached to report
Fail-Safe & Emergency Function Testing | 7.1 | Simulate instrument air loss and observe valve travel to fail position | Valve moves to defined fail position reliably | Isolation valves, stopwatch, camera | Fail action achieved within required time
| 7.2 | Simulate power loss for electric actuators | Valve goes to safe state as designed | Isolation of supply, camera | Fail-safe verified and timed
| 7.3 | De-energize solenoids to verify exhaust/vent routing supports fail travel | Solenoid exhaust permits fail movement | Hand tool, visual | Solenoids operate and exhaust correctly
| 7.4 | Record time to reach fail position | Fail time recorded and within acceptance | Stopwatch | Fail time meets safety requirements
| 7.5 | Confirm final state and reset behavior | Valve locks or resets per safety philosophy | Visual, manual reset | Final state per design
Seat Leakage & Packing Tests | 8.1 | Ensure upstream/downstream isolation and permits | Test area safe and isolated | Permit paperwork | Isolation confirmed
| 8.2 | Apply rated test pressure with valve fully closed and monitor downstream | Downstream pressure stable with acceptable leakage | Pressure source, gauge | Leakage within API/project class
| 8.3 | Use soap solution to check for external leaks at stem/bonnet | No bubbles indicating external leaks | Soap solution, flashlight | No external leaks or acceptable seepage per spec
| 8.4 | Inspect packing under pressure for seepage | Packing seepage within allowed limits | Visual | Seepage acceptable or remedial action logged
| 8.5 | If leakage exceeds limits, log NCR and perform corrective action then retest | Corrective action recorded and retest passed | Workshop tools, spares | Retest shows leakage resolved
Position Feedback & Accessories | 9.1 | Measure 4-20 mA position feedback at 0,50,100% travel | Feedback scales correctly with mechanical travel | Loop calibrator, multimeter | 4-20mA corresponds to 0-100% travel
| 9.2 | Stroke valve to actuate limit switches and confirm DCS discrete inputs | Limit switches change state and DCS shows correct status | Visual, DCS screen | Discrete inputs match mechanical status
| 9.3 | Test volume booster/relay operation under rapid stroke commands | No lag or cavitation in air supply | Rapid stroke command, visual | Volume booster operates correctly
| 9.4 | Record any alarms/fault codes from smart devices | Alarms logged and investigated | HART communicator | Fault codes resolved or logged for vendor action
DCS/PLC Integration | 10.1 | From DCS place valve in manual and send step changes; observe field movement | Field valve follows DCS commands and feedback mirrors movement | DCS access, loop calibrator | Manual commands reflected in field and DCS
| 10.2 | Auto mode dry run with simulated PVs and observe response | Valve reacts as expected to setpoint changes without oscillation | DCS, simulation tools | Loop stable and meets control requirements
| 10.3 | Verify tag names, scaling, and alarm thresholds on DCS displays | DCS shows correct tags and scaling | DCS screen, drawing | Tags and scaling match documentation
| 10.4 | Observe loop behavior for oscillation or hunting | No unwanted oscillation; record any incidents | DCS trending | Loop stable; if not, log tuning action
| 10.5 | Test interlocks and cause-and-effect where valve participates | Interlocks operate correctly under simulated conditions | Test script, DCS | Interlock behavior as designed
Common Failures Checks | 11.1 | Check for sticking/hesitation during multiple cycles | No sticking or hesitation | Manual stroke, visual | Smooth cycles; log any sticking
| 11.2 | Verify valve action direction against control signal | Valve moves in correct direction for 4-20mA | Loop calibrator | Action correct; if reversed, correct wiring
| 11.3 | Check deadband/hysteresis via ±0.5mA steps | Deadband and hysteresis acceptable | Loop calibrator | Within specified % of span
| 11.4 | Confirm stroke speed and air supply adequacy | Stroke speed meets spec | Stopwatch, pressure gauge | Air supply adequate and stroke time ok
| 11.5 | Verify fail-safe travel achieved during simulation | Fail-safe position reliable | Isolation valves, stopwatch | Fail position achieved and timed
Documentation & Handover | 12.1 | Log test dates, personnel, instruments and calibration dates | Complete test log with calibration references | Test log template, calibration certs | All instruments and calibration dates recorded
| 12.2 | Attach FAT certificates, calibration reports and device configs | All certificates attached to SAT dossier | PDF scanner/phone | Certificates present and linked
| 12.3 | Prepare acceptance statement with outstanding issues and readiness status | Clear acceptance statement produced | Word/Template | Acceptance signed by stakeholders
| 12.4 | Issue NCR for failures with root cause and retest plan | NCR logged with corrective action and schedule | NCR system/form | NCR accepted and assigned
Practical Tips | 13.1 | Photograph nameplates, orientation, and unusual conditions before repairs | Photos attached to report | Camera/Phone | Photos present
| 13.2 | Record dynamic tests (video) for future analysis | Video evidence available | Camera/Phone | Video clips attached
| 13.3 | Keep spare gaskets, packing, and filter elements on site | Spares available | Spare kit | Spares listed in toolbox