## Impulse Line Inspection Checkli
Impulse Line Inspection Excel Checklist
Step No | Inspection Item | What to Check | Service Type (Gas/Liquid/Steam) | Tools Required | Acceptance Criteria | Status (OK/Not OK) | Remarks / Action Taken | Permit Required (Yes/No) | Technician Name | Date
1 | Impulse Line Routing | Check for leakage corrosion dents mechanical damage |  | Flashlight | No visible leakage or damage |  |  | No
2 | Supports and Clamps | Check clamps tightness and absence of sagging |  | Visual Inspection | Clamps secure and properly positioned |  |  | No
3 | Temperature Touch Check | Check for abnormal cold or hot spots |  | Gloves / IR Thermometer | Uniform temperature along line |  |  | No
4 | Heat Tracing Condition | Verify tracing energized and intact |  | IR Thermometer | Heat trace functioning properly |  |  | No
5 | Insulation Condition | Check insulation coverage and sealing |  | Visual Inspection | No gaps or moisture damage |  |  | No
6 | Condensate Low Points | Inspect for condensate accumulation at low elbows | Gas/Steam | Visual / Drain Tool | No standing condensate |  |  | Yes
7 | Drain Operation | Open drain and observe condensate removal | Gas/Steam | Approved Container | Clear discharge without liquid hold up |  |  | Yes
8 | Air Venting | Vent trapped air at high points | Liquid | Hand Tools | Stable transmitter reading after vent |  |  | Yes
9 | Fittings and Joints | Inspect ferrules manifold and compression fittings |  | Visual / Ultrasonic Detector | No leakage or seepage |  |  | No
10 | Root Valve Position | Verify HP and LP fully open equalizing closed |  | Visual Check | Correct operating position |  |  | No
11 | Vibration Check | Check for excessive vibration or contact |  | Hand Check / Vibration Pen | Minimal vibration no fatigue marks |  |  | No
12 | Transmitter Response | Observe response to process change |  | DCS Trend | Fast and stable response |  |  | No
13 | Blocked Line Diagnostics | Review transmitter diagnostic status |  | Transmitter Interface | No blocked line alarm |  |  | No
14 | Purge Preparation | Confirm permit and purge media availability |  | Nitrogen / Instrument Air | Proper isolation and regulation |  |  | Yes
15 | Documentation | Record findings and raise work order if needed |  | CMMS | All actions logged properly |  |  | No