## Checklist
PLC Alarm and Trip Documentation Checklist - EPC PLC Automation Engineer Guide
Section | Item ID | Checklist Item | Description | Required | Frequency | Responsible | Evidence Filename | Status | Due Date | Comments
Document Control | DOC-001 | Executive Summary present | Executive summary describing scope, intent, and audience | Yes | Once | EPC PLC Lead | Document_Final_V1.0.docx | Not Started
Document Control | DOC-002 | Revision History template included | Revision table with version, date, author and approval columns | Yes | Once | Document Control | Document_Final_V1.0.docx | Not Started
References & Standards | REF-001 | Standards listed | IEC 61508, IEC 61511, ISA-18.2 and company standards referenced | Yes | Once | EPC PLC Lead | Document_Final_V1.0.docx | Not Started
Definitions & Priority | DEF-001 | PLC-specific definitions included | Definitions for Alarm Bit, Trip Bit, Latched Trip, etc. | Yes | Once | PLC Programmer | Document_Final_V1.0.docx | Not Started
Definitions & Priority | PRI-001 | Alarm priority definitions present | Critical, High, Medium, Low definitions with example responses | Yes | Once | EPC PLC Lead | Document_Final_V1.0.docx | Not Started
Responsibilities | RESP-001 | Responsibilities matrix completed | Roles and responsibilities for PLC Lead, Programmer, Instrument, HMI, FAT, Commissioning, Document Control | Yes | Once | EPC PLC Lead | Responsibilities_Matrix.xlsx | Not Started
Identification Workflow | ID-001 | Signal classification completed | All PLC inputs classified: Analog, Digital, Communication, Diagnostics | Yes | Once | Instrument Engineer | Signal_Classification.xlsx | Not Started
Identification Workflow | ID-002 | Alarm vs Trip decision documented | Decision logic recorded for operator-correctable, equipment damage, or safety risk | Yes | Once | EPC PLC Lead | Alarm_Trip_Decision_Log.xlsx | Not Started
Alarm Types | AT-001 | Alarm type taxonomy defined | Absolute, Deviation, ROC, Bad PV, Watchdog types defined with examples | Yes | Once | PLC Programmer | Alarm_Types.docx | Not Started
Tagging | TAG-001 | Tag naming convention enforced | Pattern <SignalType>_<LoopID>_<Condition>_<ALM/TRIP> used consistently | Yes | Once | PLC Programmer | Tag_Naming_Convention.docx | Not Started
Tagging | TAG-002 | Tag attribute records completed | Each tag has description, priority, ack req, latched, test freq, owner, bypass allowed, PLC address, data type, fail-safe state | Yes | Once | PLC Programmer | Tag_Register.csv | Not Started
Alarm Matrix | ALM-001 | Alarm & Trip Matrix created | Master matrix containing all tags, conditions, HMI messages, test freq and owner | Yes | Once/Update | EPC PLC Lead | PLC_Alarm_Matrix_v1.xlsx | Not Started
Alarm Matrix | ALM-002 | CSV header/template available | CSV header for import/export maintained for EDMS/PLC tools | Yes | Once | Document Control | Alarm_Matrix_Template.csv | Not Started
Logic Design | LD-001 | Alarm logic separation enforced | Detection, Latching, Reset, Output action separated in code (no embed in output rung) | Yes | Once | PLC Programmer | PLC_Code_Notes.pdf | Not Started
Logic Design | LD-002 | Debounce timers applied | Debounce timers for all analog alarms with documented PT value | Yes | Once | PLC Programmer | PLC_Code_Notes.pdf | Not Started
Logic Design | LD-003 | First-out logic implemented | Rising-edge detection for first-out alarms and documented logic | Yes | Once | PLC Programmer | PLC_Code_Notes.pdf | Not Started
PLC-HMI | HMI-001 | One-to-one PLC→HMI mapping verified | HMI has no derived logic; displays PLC tags only | Yes | Once | HMI Engineer | HMI_Mapping_Report.xlsx | Not Started
PLC-HMI | HMI-002 | HMI message writing rules applied | Concise, action-oriented messages; no ambiguous abbreviations; include operator action if needed | Yes | Once | HMI Engineer | HMI_Message_Guide.docx | Not Started
FAT/SAT | FAT-001 | FAT test cases prepared (100%) | Test cases for every alarm & trip prepared before FAT, using standard structure | Yes | Per FAT | FAT Team | FAT_TestCases.xlsx | Not Started
FAT/SAT | FAT-002 | Simulated inputs and forcing verified | Simulate or force inputs to validate detection, timing, latch and outputs | Yes | Per FAT | FAT Team | FAT_Results.pdf | Not Started
Routine Testing | RT-001 | Monthly alarm test log | Monthly verification of operational alarms and non-critical trips | Yes | Monthly | Maintenance | Monthly_Alarm_Test_Log.xlsx | Not Started
Routine Testing | RT-002 | Quarterly HMI–PLC cross-verification | Cross-check alarm matrix vs HMI configuration and priority colors | Yes | Quarterly | HMI Engineer | Quarterly_HMI_PLC_Report.pdf | Not Started
Routine Testing | RT-003 | Annual safety coordination test | Joint PLC–SIS test for PLC-implemented safety interface signals | Yes | Annual | Safety Lead | PLC_SIS_Coordination_Test.pdf | Not Started
Diagnostics | DIAG-001 | Diagnostic alarm testing | Monthly simulation of bad PV, sensor failure and internal diagnostics | Yes | Monthly | Instrument Engineer | Diagnostic_Test_Log.xlsx | Not Started
Watchdog/Comm | COMM-001 | Watchdog & comm test weekly | Network interruption simulation and timeout verification | Yes | Weekly | Network/PLC Support | Comm_Alarm_Test_Record.xlsx | Not Started
Post-Maintenance | PM-001 | Post-maintenance regression testing | Re-execute original test cases for affected alarms/trips before returning to service | Yes | After Maintenance | Commissioning/Maintenance | Post_Maintenance_Test_YYYYMMDD.pdf | Not Started
Change Control | CC-001 | Change control record created for every change | Reason, affected tags, impact, approvals and updated test evidence recorded | Yes | Every Change | Document Control | ChangeLog_Alarms_Project.csv | Not Started
Archiving | ARCH-001 | Records archived with revision control | All test records and matrices stored in EDMS with versioning | Yes | Continuous | Document Control | EDMS_Location_Link | Not Started
Cybersecurity | CYB-001 | Access control enforced for PLC changes | ACLs, password policies and logging for tag forcing maintained | Yes | Continuous | Cybersecurity/PLC Lead | Access_Control_Log.xlsx | Not Started
Handover | HAND-001 | Handover bundle completed | Approved alarm matrix, signed FAT/SAT records, change log and EDMS links delivered | Yes | At Handover | EPC PLC Lead | Handover_Bundle.zip | Not Started
Troubleshooting | TS-001 | Common troubleshooting steps documented | Steps for alarms not displayed, spurious alarms, intermittent alarms and latch issues | Yes | Once/Update | PLC Programmer | Troubleshooting_Guide.docx | Not Started
SOP & Training | TRAIN-001 | Operator acknowledgement procedure documented | Procedure for acknowledging alarms, actions to take, and escalation matrix | Yes | Once/Update | Operations/Training | Operator_Ack_Procedure.pdf | Not Started
SOP & Training | TRAIN-002 | FAT/SAT witness and sign-off recorded | Witness signatures captured and archived for all FAT/SAT test records | Yes | Per FAT/SAT | Commissioning Engineer | FAT_SAT_Signed_Sheets.pdf | Not Started
Deliverables | DEL-001 | Downloadable checklist and templates available | Excel checklist, CSV alarm matrix template, FAT/SAT PDF templates provided | Yes | Once/Update | Document Control | Downloads_Folder_Link | Not Started