## PV_Cross_Check
PROCESS VALUE CROSS CHECK – COMPLETE FIELD VALIDATION & AUDIT SHEET
GENERAL INFORMATION
Date | Tag ID | Loop ID | Instrument Type | Model | Serial No | Process Temp (°C) | Process Pressure (bar) | Process Condition | Reference Instrument ID | Ref Cert No | Ref Cert Expiry | Technician | Supervisor
MEASUREMENT & VALIDATION TABLE
Transmitter | Units | Local Gauge | Units | Reference | Units | Manual Calc | Units | Delta (Auto) | Tolerance | Within Tol | Action | Repeat 1 | Repeat 2 | Repeat 3 | Std Dev (Auto) | Notes
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
[8 empty] | 0 |  | PASS |  |  |  |  | #DIV/0!
FIELD CHECKLIST (Mandatory Before Close-Out)
LOTO & Permit Verified | No
Process Stable Confirmed | No
Reference Instrument Calibration Valid | No
Impulse Tubing Inspected | No
Earthing & Wiring Checked | No
Repeatability Verified | No
Manual Calculation Performed | No
Delta Compared with Tolerance | No
Escalation Raised if Required | No
Results Logged in CMMS / Historian | No
SUMMARY
Total Records | 0
Total PASS | 40
Total FAIL | 0

## all in one
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39
Step No | Task | Details | Done
1 | Record tag, loop identifier, instrument model and last calibration date | Fill Tag ID, Loop, Model, Last Cal Date | No
2 | Confirm process conditions (temperature, pressure, steady/transient) | Note temp, pressure, flow state | No
3 | Follow isolation and LOTO procedures, notify operations | Attach permit reference | No
4 | Verify temporary reference instrument calibration certificate & battery | Record Ref ID and certificate expiry | No
5 | Stabilize measurement (allow process to stabilise if safe) | Wait time (mins) and observation | No
6 | Record three repeatability readings for each source (Transmitter/Gauge/Reference) | R1,R2,R3 for each | No
7 | Perform manual calculation where applicable (record assumptions) | Include formula and inputs | No
8 | Inspect impulse tubing, valves, connectors, earthing | Note any wetting, air, vibration | No
9 | Calculate delta and compare with site tolerance | Convert % tolerance to engineering units | No
10 | Determine action: Monitor / Recalibrate / Repair / Replace | Choose and add Work Order if required | No
11 | Attach calibration certificate images and reference instrument evidence | Attach file names or links | No
12 | Log results into historian and include in shift handover | Indicate historian tag or ticket | No
13 | If delta exceeds tolerance, auto-generate a maintenance work order | Record WO# and planned date | No
14 | Update transmitter configuration if configuration error found | Record old/new settings and authoriser | No
15 | Close permit and sign off with technician & supervisor | Name and timestamp | No
Timestamp | Tag ID | Loop/Loop ID | Instrument Type | Instrument Model | Serial No | Transmitter Reading | Transmitter Units | Local Gauge Reading | Local Gauge Units | Temporary Reference Reading | Reference Units | Manual Calculation Result | Calc Units | Delta (eng units) | Tolerance (eng units) | Within Tolerance (Y/N) | Action Taken | Technician | Supervisor | Process Temperature (Â°C) | Process Pressure (bar) | Process Condition (steady/transient) | R1_Transmitter | R2_Transmitter | R3_Transmitter | R1_Gauge | R2_Gauge | R3_Gauge | R1_Ref | R2_Ref | R3_Ref | Impulse Tubing Status | Valve Positions | Earthing OK (Y/N) | Reference Instrument ID | Ref Certificate Expiry Date | Notes | Follow-up WO# | Planned WO Date
2026-02-12T10:12:00 | FT 205 | Loop-FT205 | DP Flow Transmitter | Model X-100 | SN12345 | 560 | L/min |  |  | 547 | L/min | 547 | L/min | 13 | L/min | No | Monitor | Tech A | Sup B | 25 | 3.2 | steady | 560 | 560 | 560 |  |  |  | 547 | 547 | 547 | Wet impulse tubing | Open | Yes | PIT-01 | 2025-12-31 | Pipe vibration, repeat and verify pitot calibration | WO-789 | 2026-02-20
Condition | Likely Cause | Immediate Action
Constant offset (difference constant across range) | Calibration/configuration error | Check zero/span, engineering units and range; verify config backup
Offset varies with temperature | Density compensation or temp correction issue | Verify density value, temperature compensation curves, perform temp sweep if safe
Large random scatter | Blocked impulse tubing, loose connectors, electrical noise | Inspect impulse tubing, tighten connectors, check power supply ripple and earthing
Difference increases with signal amplitude | Linearity/span issue or range mismatch | Check transmitter linearity, perform multi-point verification, check range/span settings
Gauge and reference agree but transmitter differs | Transmitter electronics/config error | Check configuration, replace transmitter if fails bench test
Reference agrees with transmitter but gauge differs | Gauge mechanical error or parallax | Inspect/replace gauge, clean sight glass, check impulse tubing between gauge and vessel
Field | Value
Reference Instrument ID
Manufacturer / Model
Instrument Serial No
Calibration Lab
Calibration Certificate No
Calibration Date
Calibration Due Date
Declared Uncertainty / Accuracy
Attach Image Filename / Link
Technician who verified certificate
Loop Criticality | Suggested Frequency | Notes
Critical Safety Loop | Daily to Weekly | Use daily checks for fast-changing critical loops; trend in historian
Important Control Loop | Weekly to Monthly | Adjust based on failure history and impact
Monitoring Loop | Quarterly | Lower frequency unless evidence of drift
Low Risk / Non-critical | Biannual or Annual | Use risk-based approach