## Checklist
Closed Tank DP Level Transmitter Troubleshooting Checklist
Step-by-Step Field Checklist for Instrumentation, Maintenance, and Commissioning Engineers
Use during field troubleshooting in the sequence shown. Start with safety and process verification, then move from loop power to wiring, PLC/DCS, manifold, impulse lines, wet/dry leg, density, calibration, hardware, and smart diagnostics.
Step No. | Category / Section | Checklist Item | What to Check | Expected Condition | Abnormal Observation | Likely Cause | Corrective Action | Priority (High / Medium / Low) | Safety Critical (Yes / No) | Status (Not Checked / OK / Fault / N/A) | Remarks
1. Safety, Isolation, and Process Verification
1.1 | 1. Safety, Isolation, and Process Verification | Apply LOTO and make the work area safe | Confirm isolation permit, LOTO status, and access control before opening any impulse line, manifold, or drain point. | LOTO active; work permit approved; area isolated; PPE available. | No permit, live process, uncertain isolation, or unsafe access. | Incomplete isolation; permit gap; poor coordination. | Stop work, isolate correctly, obtain permit approval, and verify safe access before proceeding. | High | Yes | Not Checked
1.2 | 1. Safety, Isolation, and Process Verification | Confirm tank pressure / vacuum condition | Check vessel pressure, vacuum, vent status, and any trapped pressure in impulse lines or wet leg reference leg. | Tank and connected lines at safe pressure for maintenance activity. | Unexpected pressure, vacuum pull, or trapped pressure after isolation. | Residual pressure; blocked vent; wrong valve lineup. | Depressurize slowly, verify venting path, and confirm zero energy state before loosening fittings. | High | Yes | Not Checked
1.3 | 1. Safety, Isolation, and Process Verification | Review process hazard before handling lines | Confirm fluid service, temperature, toxicity, flammability, corrosiveness, and contamination risk. | Service understood and correct PPE selected. | Unknown service or unsuitable PPE. | Incomplete process information. | Obtain SDS/process data and upgrade PPE before opening the loop. | High | Yes | Not Checked
1.4 | 1. Safety, Isolation, and Process Verification | Check for leaks before touch-up work | Inspect manifold, fittings, impulse tubing, drains, and vents for seepage or spray before direct contact. | No visible leak, no odor, no hissing, no staining. | Leakage, wet insulation, chemical smell, frost, or spray marks. | Loose fitting; cracked tubing; failed gasket; valve passing. | Isolate, contain, repair leak, then re-test for tightness. | High | Yes | Not Checked
2. Actual Tank Level Verification
2.1 | 2. Actual Tank Level Verification | Confirm the real tank level independently | Compare transmitter indication with sight glass, local gauge, dip measurement, operator observation, or backup transmitter. | Independent verification matches expected process condition. | DCS shows a level that does not match actual tank condition. | Fault may be on process side, transmitter, or control system. | Do not calibrate blindly; locate the fault branch by comparing field vs DCS value. | High | No | Not Checked
2.2 | 2. Actual Tank Level Verification | Assess the error pattern | Classify the symptom: high at empty, low at full, fixed, fluctuating, drifting, or reversed response. | Error pattern is stable and repeatable enough to guide diagnosis. | Reading pattern does not match real level behavior. | Useful clue for wet leg, dry leg, impulse line, scaling, or valve lineup issue. | Use symptom pattern to decide which branch to inspect first. | High | No | Not Checked
2.3 | 2. Actual Tank Level Verification | Compare local display with DCS/PLC value | Check transmitter local display, DCS value, and raw/current value together. | All indications agree or the mismatch points to a clear fault domain. | Local transmitter good, DCS wrong; or both wrong but in different ways. | Wiring, analog input, scaling, or transmitter issue. | Use the mismatch to separate field problem from control-system problem. | High | No | Not Checked
3. Loop Power and Continuity
3.1 | 3. Loop Power and Continuity | Measure 24 VDC loop supply at field and panel | Check supply voltage at transmitter terminals and panel side under load. | Stable 24 VDC within design range. | Low voltage, unstable supply, or no supply. | Power supply failure; fuse open; excessive loop burden. | Repair supply, replace fuse, or remove excessive burden. | High | Yes | Not Checked
3.2 | 3. Loop Power and Continuity | Verify loop current with a meter | Measure current at the transmitter and compare it with the control-room indication. | Measured loop current matches indicated process value. | Field current and DCS current do not match. | Signal path fault between transmitter and control system. | Trace the mismatch point: transmitter, cable, barrier, AI module, or configuration. | High | Yes | Not Checked
3.3 | 3. Loop Power and Continuity | Check continuity and polarity | Confirm positive and negative loop conductors, ferrules, and terminal tightness. | Correct polarity and continuous loop. | 0 mA, intermittent output, reversed polarity, or open circuit. | Broken wire; loose termination; reversed wiring. | Correct polarity, tighten terminals, and replace damaged cable sections. | High | Yes | Not Checked
3.4 | 3. Loop Power and Continuity | Inspect for moisture and corrosion in junction box | Open the junction box and check glands, terminals, shields, and seal condition. | Dry, clean, and mechanically sound terminals. | Condensation, green corrosion, salt deposits, or water entry. | Ingress through gland or cover; poor sealing. | Dry out, clean, reseal, and replace damaged glands or terminals. | Medium | Yes | Not Checked
4. Wiring from Field to PLC / DCS
4.1 | 4. Wiring from Field to PLC / DCS | Trace the complete signal path | Follow transmitter -> junction box -> marshalling -> barrier/isolator -> AI module -> PLC/DCS tag -> HMI/SCADA. | Each link mapped correctly and documented. | Missing or uncertain link in the chain. | Wrong tag mapping or undocumented reroute. | Document the actual signal path and correct the mismatch. | High | No | Not Checked
4.2 | 4. Wiring from Field to PLC / DCS | Check for wrong terminal or wrong pair | Verify core pair, terminal number, marshalling point, and channel assignment. | Field pair lands on the correct AI channel. | Wrong pair, swapped terminals, or channel mismatch. | Installation wiring error. | Re-terminate to the correct pair and update drawings/as-built records. | High | Yes | Not Checked
4.3 | 4. Wiring from Field to PLC / DCS | Check shield grounding practice | Verify shield termination method and grounding point. | Shield grounded per site standard, normally one end only for analog signal integrity. | Noise, unstable reading, or shield grounded both ends incorrectly. | Ground loop / induced noise / poor EMC practice. | Correct shield termination and improve cable routing away from noise sources. | Medium | No | Not Checked
4.4 | 4. Wiring from Field to PLC / DCS | Check AI module health and channel mapping | Review module status, channel diagnostics, and tag binding in PLC/DCS. | Healthy card, correct channel, correct tag, and valid signal quality. | Field output changes but PLC value stays fixed or wrong. | AI module failure; wrong channel; bad tag mapping. | Repair module, remap tag, or reassign the input channel. | High | No | Not Checked
4.5 | 4. Wiring from Field to PLC / DCS | Check for noise pickup / intermittent faults | Move cables gently, inspect glands, and review trend noise versus field stability. | Stable trend that follows actual process behavior. | Fluctuation, spikes, or dropouts when cables are moved. | Loose termination; broken conductor strand; EMI. | Repair termination, replace cable, and separate from power cabling. | Medium | No | Not Checked
5. PLC / DCS Configuration and Scaling
5.1 | 5. PLC / DCS Configuration and Scaling | Verify tag name, range, and engineering units | Check the configured LRV, URV, tank height, and engineering unit in the AI block. | Values match the instrument range and tank geometry. | Wrong range, wrong units, or wrong tank height entered. | Configuration error. | Correct the tag parameters and re-test from raw input to displayed level. | High | No | Not Checked
5.2 | 5. PLC / DCS Configuration and Scaling | Verify 4–20 mA scaling | Confirm current-to-engineering-value conversion is correct and not reversed. | 4 mA = LRV and 20 mA = URV for the intended action. | Reverse action, wrong input type, or incorrect scaling map. | Wrong analog conversion setup. | Correct scaling and validate the output with a simulated loop value. | High | No | Not Checked
5.3 | 5. PLC / DCS Configuration and Scaling | Check for forced value / manual override / simulation | Inspect logic for hold, force, simulation, maintenance, or bad-quality override. | No active override and live value passes through normally. | Reading frozen even though transmitter output changes. | Logic hold; simulation; forced value. | Remove override, end simulation, and return the point to auto. | High | No | Not Checked
5.4 | 5. PLC / DCS Configuration and Scaling | Review raw counts versus engineering value | Compare raw AI counts with scaled display value. | Raw counts and engineering value change consistently. | Raw counts change but engineering value does not, or vice versa. | Scaling logic fault or AI interpretation error. | Correct the conversion block and verify trend response. | High | No | Not Checked
5.5 | 5. PLC / DCS Configuration and Scaling | Check bad quality / diagnostics flags | Review module fault bits, channel status, and data quality flags. | Signal quality healthy. | Bad quality, fault state, or stale data. | AI module fault; communication issue; data hold. | Clear hardware fault and ensure the DCS is reading the live channel. | High | No | Not Checked
6. Manifold Valve Position
6.1 | 6. Manifold Valve Position | Confirm normal manifold lineup | For standard DP service, verify HP open, LP open, equalizing closed, drain/vent closed unless troubleshooting. | Correct operating lineup restored after maintenance. | Equalizing valve left open or root valve closed. | Incorrect valve position after maintenance. | Reset manifold to normal operating position and re-check reading. | High | Yes | Not Checked
6.2 | 6. Manifold Valve Position | Check for valve passing or leakage | Inspect equalizing, vent, and drain valves for internal leakage or incomplete shutoff. | Valve seats tight and no bypass flow. | Reading offset or unchanged despite valve movement. | Internal passing, worn seat, damaged valve packing. | Repair or replace the faulty valve and repeat the zero check. | High | Yes | Not Checked
6.3 | 6. Manifold Valve Position | Check symptom after valve lineup change | Observe transmitter after restoring manifold to normal operating mode. | Reading returns to a credible level and follows process changes. | Constant or misleading reading after maintenance. | Valve lineup error or trapped differential pressure. | Re-bleed safely, equalize if required, and confirm correct operating sequence. | High | Yes | Not Checked
7. Impulse Line Inspection
7.1 | 7. Impulse Line Inspection | Inspect both HP and LP impulse lines | Check for sludge, rust, scale, wax, crystals, slurry, polymer, or trapped liquid/gas. | Lines are clean, intact, and properly sloped. | Slow, frozen, drifting, or unstable response. | Partial/complete blockage or trapped medium. | Clean, flush, or replace the affected line and verify slope. | High | Yes | Not Checked
7.2 | 7. Impulse Line Inspection | Check for slope and draining issues | Confirm the installation has correct fall/rise and no low pockets that trap fluid or gas. | Impulse lines drain or vent as intended by design. | Air pockets, liquid pockets, or delayed response. | Incorrect slope or bad routing. | Re-route or re-support the tubing to the required slope. | High | Yes | Not Checked
7.3 | 7. Impulse Line Inspection | Check for kink, crack, vibration damage, or leakage | Inspect tubing mechanically along the full run and at supports and bends. | No physical damage or seepage. | Kinked tubing, cracked ferrule, wet points, or vibration wear. | Mechanical damage from vibration or poor support. | Replace damaged tubing and add supports/vibration control. | High | Yes | Not Checked
7.4 | 7. Impulse Line Inspection | Test whether tapping changes reading | Gently tap the line where permitted and watch whether the reading responds. | No false change from tapping. | Reading jumps or changes after tapping. | Sticky deposit or partial blockage. | Treat as a blockage warning; clean or flush the affected section. | Medium | No | Not Checked
8. Wet Leg and Dry Leg Condition
8.1 | 8. Wet Leg and Dry Leg Condition | Confirm wet leg is truly full | Check fill condition, reference liquid level, and any leakage/evaporation loss. | Wet leg remains full and stable. | False high reading, especially when tank is empty. | Wet leg empty or partially drained; loss of reference head. | Refill and secure the wet leg; inspect for leaks or evaporation loss. | High | Yes | Not Checked
8.2 | 8. Wet Leg and Dry Leg Condition | Confirm wet leg reference density | Verify the reference liquid is the correct fluid and density for the calculation. | Reference density matches design assumption. | Offset reading that changes over time or after maintenance. | Wrong reference liquid or changed density. | Correct the fill fluid and update any compensation settings. | High | No | Not Checked
8.3 | 8. Wet Leg and Dry Leg Condition | Confirm dry leg remains dry | Inspect the vapor leg for condensation, liquid accumulation, or plugging. | Dry leg is free of liquid and blockage. | False low reading or unstable output. | Dry leg filled with condensate or blocked vapor line. | Drain, clear, and re-establish a dry reference path. | High | Yes | Not Checked
8.4 | 8. Wet Leg and Dry Leg Condition | Check for condensate management and purge condition | Review heat tracing, insulation, drain arrangement, and periodic maintenance. | No unmanaged condensation or buildup. | Repeated offset or drifting with temperature changes. | Condensation management failure. | Correct heat tracing, insulation, or drain maintenance routine. | Medium | No | Not Checked
9. Density / Specific Gravity Checks
9.1 | 9. Density / Specific Gravity Checks | Review actual process density / SG | Check whether product composition, temperature, concentration, or batching has changed. | Measured SG matches design or is compensated in the logic. | Different level reading for the same actual height. | Density variation or wrong SG assumption. | Update calculations or apply compensation if the process requires it. | High | No | Not Checked
9.2 | 9. Density / Specific Gravity Checks | Check temperature-linked drift | Correlate level reading with temperature trend and operating batch conditions. | Reading remains consistent across normal temperature range. | Reading drifts as temperature changes. | Density change or wet leg density shift. | Review SG correction, temperature effect, and process conditions. | Medium | No | Not Checked
9.3 | 9. Density / Specific Gravity Checks | Check slurry / layering / mix variation | Look for suspended solids, stratification, or different batches producing different readings. | Process condition stable and repeatable. | Inconsistent output for the same nominal fill. | Layering, concentration variation, or non-uniform liquid head. | Validate whether DP measurement is suitable or needs compensation. | Medium | No | Not Checked
10. Calibration, Zero, and Span
10.1 | 10. Calibration, Zero, and Span | Verify zero with proper isolation and reference condition | Isolate and apply the correct zero condition before judging transmitter output. | Zero value matches expected DP at the reference point. | Zero shifted after maintenance or reinstall. | Improper zero trim; wet leg reference error. | Perform zero trim only after the process reference condition is verified. | High | Yes | Not Checked
10.2 | 10. Calibration, Zero, and Span | Verify span / URV / LRV | Confirm transmitter range, tank height, and span match the actual installation. | Instrument range matches the tank geometry. | Wrong tank height, wrong LRV/URV, or saturated output. | Incorrect ranged instrument or wrong calibration data. | Re-range the transmitter and update the DCS scaling accordingly. | High | No | Not Checked
10.3 | 10. Calibration, Zero, and Span | Check linearity and output at known points | Apply known DP points and compare expected versus actual mA output. | Output tracks linearly across the range. | Nonlinear response, offset, or slope error. | Calibration drift or sensor issue. | Re-trim the device; replace if linearity cannot be restored. | High | Yes | Not Checked
10.4 | 10. Calibration, Zero, and Span | Confirm unit conversion and level-to-pressure logic | Verify the engineering calculation uses the correct density and reference height. | Converted level matches design calculation. | Calculation error or wrong units displayed. | Wrong unit conversion or wrong level formula. | Correct the conversion logic and re-test with a known condition. | Medium | No | Not Checked
11. Transmitter Hardware Checks
11.1 | 11. Transmitter Hardware Checks | Inspect diaphragm / process port condition | Check for diaphragm damage, coating, plugging, or deformation at the process connection. | Sensor surfaces intact and unobstructed. | No output change with applied DP or unstable output under steady condition. | Sensor damage, blockage, or contamination. | Clean, repair, or replace the transmitter as required. | High | Yes | Not Checked
11.2 | 11. Transmitter Hardware Checks | Check electronics and display health | Look for blank display, failed electronics, or internal fault messages. | Display and electronics respond normally. | Display dead, frozen, or full of internal alarms. | Electronic board failure or internal damage. | Repair or replace transmitter electronics. | High | No | Not Checked
11.3 | 11. Transmitter Hardware Checks | Check for moisture ingress or corrosion | Inspect housing, cable entry, terminal board, and electronics compartment. | Dry interior and intact seals. | Corrosion, water droplets, or damaged seals. | Ingress due to damaged sealing or poor gland practice. | Dry, clean, reseal, and replace gaskets or gland components. | High | Yes | Not Checked
11.4 | 11. Transmitter Hardware Checks | Verify transmitter responds to a known test DP | Use a calibrated source or test arrangement and observe whether output moves correctly. | Stable, repeatable output response. | Output stuck, erratic, or impossible to trim. | Internal sensor or electronics failure. | Replace the defective transmitter after external causes are cleared. | High | No | Not Checked
12. Smart Communication and Diagnostics
12.1 | 12. Smart Communication and Diagnostics | Check device status and diagnostics | Review HART / Fieldbus / smart device diagnostic codes, PV status, and warnings. | Device reports healthy status or a known recoverable alert. | PV invalid, alarm state, or unreported device fault. | Smart device diagnostic condition. | Read and resolve the device diagnostic before changing calibration. | High | No | Not Checked
12.2 | 12. Smart Communication and Diagnostics | Confirm digital value matches analog output | Compare digital PV with the 4–20 mA output and the DCS readout. | Digital and analog values agree. | Digital looks correct but analog does not, or vice versa. | Analog output issue, scaling mismatch, or communication error. | Identify whether the fault is in the analog path or the digital data path. | High | No | Not Checked
12.3 | 12. Smart Communication and Diagnostics | Check simulation / write protection / damping | Verify device is not in simulation mode, write-protected incorrectly, or over-damped. | Normal operating mode and suitable damping. | Frozen value, slow response, or commissioning value left active. | Simulation mode; wrong damping; configuration hold. | Exit simulation, remove temporary settings, and return to normal service. | Medium | No | Not Checked
12.4 | 12. Smart Communication and Diagnostics | Check comms quality and asset integration | Verify HART multidrop, gateway, marshalling interface, and asset-management visibility. | Communication stable and data current. | Comms fault or stale data in DCS/asset tool. | Gateway issue; comms wiring; data mapping fault. | Repair communication path and refresh the host system. | Medium | No | Not Checked
13. Symptom-Based Cross-Check
13.1 | 13. Symptom-Based Cross-Check | Reading high when tank is empty | Check wet leg full condition, LP reference loss, equalizing valve position, and zero shift. | Level should be near zero or minimum for the tank condition. | False high indication at empty tank. | Wet leg empty; LP lost; manifold error; zero offset. | Restore reference leg, correct valve lineup, and re-zero after verification. | High | Yes | Not Checked
13.2 | 13. Symptom-Based Cross-Check | Reading low when tank is full | Check HP impulse blockage, dry leg condensation, range setup, and span calibration. | Level should read near full or maximum expected value. | False low indication at full tank. | Blocked HP line; dry leg filled; wrong span; scaling error. | Clear line blockage, restore dry leg, and verify span/range. | High | Yes | Not Checked
13.3 | 13. Symptom-Based Cross-Check | Reading fluctuates | Check air/gas in line, loose wiring, process pulsation, poor grounding, and unstable tank pressure. | Stable signal that follows actual level movement. | Spikes, hunting, or unstable reading. | Air pocket; vibration; grounding fault; noisy AI input. | Remove air pockets, secure wiring, improve grounding, and stabilize the process reference. | High | No | Not Checked
13.4 | 13. Symptom-Based Cross-Check | Reading is constant / frozen | Check equalizing valve, blocked impulse line, transmitter freeze, PLC hold, and input card status. | Reading should move when actual level changes. | No response to actual process change. | Equalizing valve open; blockage; PLC override; AI fault. | Restore valve lineup, clear blockage, release hold, and confirm AI health. | High | No | Not Checked
13.5 | 13. Symptom-Based Cross-Check | No output | Check loop supply, open circuit, broken loop, transmitter electronics, and terminal continuity. | A valid current signal is present. | 0 mA or no valid signal. | Power loss; open loop; transmitter failure. | Restore supply and continuity; replace electronics if the loop remains dead. | High | Yes | Not Checked
14. Final Troubleshooting Order
14.1 | 14. Final Troubleshooting Order | 1) Verify actual tank level and compare with DCS/local indication. | Follow the sequence exactly in field work. | Use this order to avoid blind replacement. | Random troubleshooting, skipped checks, or repeated work. | Not following a structured sequence. | Return to the first unresolved step and continue in order. | High | No | N/A
14.2 | 14. Final Troubleshooting Order | 2) Apply safety isolation, LOTO, and confirm pressure-free condition. | Follow the sequence exactly in field work. | Use this order to avoid blind replacement. | Random troubleshooting, skipped checks, or repeated work. | Not following a structured sequence. | Return to the first unresolved step and continue in order. | High | No | N/A
14.3 | 14. Final Troubleshooting Order | 3) Confirm loop power, continuity, and measured loop current. | Follow the sequence exactly in field work. | Use this order to avoid blind replacement. | Random troubleshooting, skipped checks, or repeated work. | Not following a structured sequence. | Return to the first unresolved step and continue in order. | High | No | N/A
14.4 | 14. Final Troubleshooting Order | 4) Trace wiring from field transmitter to PLC/DCS input. | Follow the sequence exactly in field work. | Use this order to avoid blind replacement. | Random troubleshooting, skipped checks, or repeated work. | Not following a structured sequence. | Return to the first unresolved step and continue in order. | High | No | N/A
14.5 | 14. Final Troubleshooting Order | 5) Check PLC/DCS tag, scaling, raw counts, and override states. | Follow the sequence exactly in field work. | Use this order to avoid blind replacement. | Random troubleshooting, skipped checks, or repeated work. | Not following a structured sequence. | Return to the first unresolved step and continue in order. | High | No | N/A
14.6 | 14. Final Troubleshooting Order | 6) Verify manifold valves are in the correct operating lineup. | Follow the sequence exactly in field work. | Use this order to avoid blind replacement. | Random troubleshooting, skipped checks, or repeated work. | Not following a structured sequence. | Return to the first unresolved step and continue in order. | High | No | N/A
14.7 | 14. Final Troubleshooting Order | 7) Inspect impulse lines for blockage, leakage, slope, and trapped fluid. | Follow the sequence exactly in field work. | Use this order to avoid blind replacement. | Random troubleshooting, skipped checks, or repeated work. | Not following a structured sequence. | Return to the first unresolved step and continue in order. | High | No | N/A
14.8 | 14. Final Troubleshooting Order | 8) Confirm wet leg / dry leg condition and reference integrity. | Follow the sequence exactly in field work. | Use this order to avoid blind replacement. | Random troubleshooting, skipped checks, or repeated work. | Not following a structured sequence. | Return to the first unresolved step and continue in order. | High | No | N/A
14.9 | 14. Final Troubleshooting Order | 9) Review density / specific gravity changes and process temperature effects. | Follow the sequence exactly in field work. | Use this order to avoid blind replacement. | Random troubleshooting, skipped checks, or repeated work. | Not following a structured sequence. | Return to the first unresolved step and continue in order. | High | No | N/A
14.10 | 14. Final Troubleshooting Order | 10) Verify calibration, zero, span, and linearly expected output. | Follow the sequence exactly in field work. | Use this order to avoid blind replacement. | Random troubleshooting, skipped checks, or repeated work. | Not following a structured sequence. | Return to the first unresolved step and continue in order. | High | No | N/A
14.11 | 14. Final Troubleshooting Order | 11) Inspect transmitter hardware for sensor, seal, or electronics failure. | Follow the sequence exactly in field work. | Use this order to avoid blind replacement. | Random troubleshooting, skipped checks, or repeated work. | Not following a structured sequence. | Return to the first unresolved step and continue in order. | High | No | N/A
14.12 | 14. Final Troubleshooting Order | 12) Check smart communication, diagnostics, simulation, and device status. | Follow the sequence exactly in field work. | Use this order to avoid blind replacement. | Random troubleshooting, skipped checks, or repeated work. | Not following a structured sequence. | Return to the first unresolved step and continue in order. | High | No | N/A

## How to Use
How to Use This Checklist
1 | Start with safety and actual tank verification before touching calibration.
2 | Mark each row Status as OK, Fault, Not Checked, or N/A during the field walkdown.
3 | Use the abnormal observation and likely cause columns to isolate the fault branch.
4 | Treat high-priority and safety-critical rows first.
5 | After the fault is corrected, recheck the symptom at the source and at the DCS/PLC.