## Checklist
ON OFF CONTROL VALVE SELECTION CHECKLIST (EPC ENGINEERING)
Section | Checklist Item | Yes | No | N.A. | Remarks | Responsible | Priority | Status
Process | Define the actual process duty clearly, including whether the valve is intended for isolation, shutdown, interlock action, emergency shutdown, or normal line switching. | [6 empty] | Pending
Process | Confirm whether the valve will be used in a batch operation or a continuous process, because cyclic duty and steady-state duty create different reliability and maintenance expectations. | [6 empty] | Pending
Process | State the process action in plain engineering terms so the safe-state philosophy, operating philosophy, and cause-and-effect logic are aligned from the beginning. | [6 empty] | Pending
Fluid | Identify the fluid type in detail, including whether it is clean liquid, gas, hydrocarbon, corrosive chemical, viscous fluid, or slurry with solids. | [6 empty] | Pending
Fluid | Check suspended solids, sand, scale, or other abrasive content that could damage seats, trim, sealing surfaces, or internal moving parts. | [6 empty] | Pending
Fluid | Assess whether the service may polymerize, crystallize, foul, or chemically attack wetted parts during normal operation or shutdown conditions. | [6 empty] | Pending
Operating | Confirm the operating pressure, normal pressure, design pressure, operating temperature, and normal temperature for the service. | [6 empty] | Pending
Operating | Check maximum excursions, including upset conditions, startup/shutdown transients, and any abnormal temperature or pressure peaks. | [6 empty] | Pending
Shutoff | Define the required shutoff class and leakage expectation, whether zero visible leakage, tight isolation, or standard isolation is acceptable. | [6 empty] | Pending
Valve | Compare ball, gate, butterfly, plug, knife gate, and diaphragm valve options before selecting the final ON/OFF duty valve type. | [6 empty] | Pending
Actuator | Select the actuator type based on utility availability, closing speed requirement, force requirement, and project preference for pneumatic, electric, or hydraulic actuation. | [6 empty] | Pending
Safety | Specify the fail-safe position clearly as fail-close, fail-open, or fail-last so the valve behavior matches the plant protection philosophy. | [6 empty] | Pending
Sizing | Check required flow capacity, pressure drop, and Cv sizing to ensure the valve performs the duty without excessive restriction or unstable operation. | [6 empty] | Pending
Sizing | Avoid oversizing because an oversized ON/OFF valve can reduce seat loading, affect shutoff reliability, and increase wear during repeated cycling. | [6 empty] | Pending
Material | Verify body, trim, seat, packing, seal, and lining materials against corrosion, erosion, chloride content, temperature, and sour service concerns. | [6 empty] | Pending
Installation | Review field access, maintenance clearance, actuator removal space, manual override access, and the ability to inspect the valve safely. | [6 empty] | Pending
Accessories | Confirm whether the valve needs a solenoid valve, limit switches, position feedback, air set, handwheel, or manual override arrangement. | [6 empty] | Pending
Performance | Verify opening and closing time requirements so the selected actuator and valve combination meets shutdown or interlock response needs. | [6 empty] | Pending
Maintenance | Check future maintenance expectations, including seat replacement, actuator servicing, inspection access, and spare part availability. | [6 empty] | Pending
Vendor | Confirm vendor compliance with the project specification, datasheet, P&ID intent, materials, shutoff class, and all technical notes. | [6 empty] | Pending
ENGINEERING SUMMARY
Total Checklist Items | 20
Items Checked Yes | 0
Items Marked No | 20
Items Marked N.A. | 0
Completion Percentage | 0%
Outstanding Critical Items | 0

## Decision Matrix
VALVE SELECTION DECISION MATRIX
Application | Valve Type | Reason | Advantage | Limitations | Use Case
Clean fluid | Ball valve | Use a ball valve when the service is clean and the project needs tight shutoff, quick quarter-turn action, and low pressure loss. | Very good shutoff and fast operation. | Not ideal for abrasive contamination if solids are present. | Clean process lines, utility isolation, and shutdown service.
Slurry | Knife gate or ball valve | Use a knife gate valve or a suitably designed ball valve when the medium contains solids, fibers, or abrasive slurry that can damage standard trim. | Better tolerance to solids and difficult service. | Seat wear and sealing concerns must be reviewed carefully. | Slurry transfer, dirty drain lines, and solids-handling duties.
Corrosive service | Diaphragm valve | Use a diaphragm valve when chemical resistance is more important than compact cost and the process fluid must be isolated from moving parts. | Excellent chemical isolation and contamination control. | Pressure and temperature limits may be lower than other styles. | Chemical dosing, corrosive lines, and contaminated utility service.
High pressure service | Gate valve | Use a gate valve when high pressure strength and very low pressure drop in the open position are important engineering requirements. | Strong construction and low open-flow resistance. | Not suitable for frequent cycling or fast response duty. | High-pressure isolation and large bore lines.
Fast shutdown | Ball valve | Select a ball valve for emergency shutdown or rapid isolation where quick quarter-turn action and dependable shutoff are required. | Fast closure with strong shutoff performance. | Seat wear should be monitored in frequent cycling service. | ESD, trip isolation, and fast acting shutdown service.
Utility service | Butterfly valve | Use a butterfly valve for utility service when economical pricing, compact size, and suitability for large diameters are priorities. | Lightweight and cost-effective for large line sizes. | Leakage performance may be less demanding than soft-seat ball valves. | Cooling water, air, and general utility headers.
Switching service | Plug valve | Use a plug valve where the service needs quick switching, moderate fouling resistance, and a simple quarter-turn operating principle. | Good for fast operation and switching duty. | Maintenance and sealing must be considered for dirty service. | Line switching, hydrocarbon service, and selected chemical duties.
Note: Final valve selection must always consider process duty, shutoff requirement, fluid characteristics, actuator logic, fail-safe position, installation access, and maintenance practicality.

## Mistakes & Case Study
COMMON MISTAKES IN ON OFF VALVE SELECTION | REAL INDUSTRIAL CASE STUDY
Using a control valve instead of a true ON/OFF valve, which weakens shutoff reliability and creates poor isolation performance. | Project scenario: A batch reactor feed line in a chemical plant requires an isolation valve that can close immediately during a high-level trip and prevent reverse leakage into the reactor.
Oversizing the valve, which can reduce seat loading, weaken sealing performance, and increase long-term wear. | Engineering requirement: The valve must provide tight shutoff, fast closure, reliable trip integration, and acceptable performance in moderately corrosive service.
Ignoring fail-safe logic, which can cause the valve to move in the wrong direction or remain unsafe during loss of air, power, or signal. | Selection logic: The team compares a diaphragm valve and a lined ball valve, checking fluid compatibility, response speed, shutoff class, actuator force, and maintenance access.
Not checking cavitation and flashing, which may damage trim, seats, or internal parts even in a nominal ON/OFF duty valve. | Final decision: A fail-close pneumatic ball valve with suitable lining is selected where the service and material compatibility support the duty.
Ignoring installation space, including actuator removal clearance, tubing access, manual override access, and maintenance reach. | Reason for choice: The selected valve provides a strong combination of rapid action, dependable shutoff, and practical maintenance access for EPC operation.
Selecting the wrong body or seat material, which can lead to corrosion, erosion, swelling, leakage, or early failure. | Lessons learned: The best selection is made by following process duty, safe-state philosophy, and material compatibility rather than choosing by habit alone.
Skipping response-time verification, which can cause the valve to miss shutdown timing or fail to meet trip logic requirements.
Missing accessory requirements such as limit switches, solenoid valves, position feedback, or handwheel/manual override.
Why these mistakes matter | Case study takeaway
These mistakes usually appear during design review, procurement, or late field checks and can create rework, leakage, or shutdown reliability issues. | The final selection should be validated against process conditions, trip philosophy, service compatibility, and maintenance practicality.