## Checklist
Anti-Surge Control Valve Selection and Sizing Checklist
Detailed engineering checklist— use this sheet for design review, vendor comparison, and commissioning tracking.
Total Items |  | Completed |  | In Progress |  | High Priority |  | How to use 1. Fill Status, Priority, Owner, Target Date, Remarks. 2. Keep the checklist aligned with OEM data and commissioning evidence.
45 |  | 1 |  | 2 |  | 1
Section | Checklist Item | Detailed Requirement | Engineering Reason | Typical Range / Value | Verification Method | Status | Priority | Owner | Target Date | Remarks
Compressor data & surge basis | Compressor service | Confirm whether the duty is centrifugal compressor recycle, axial compressor protection, or another special compression service. | Compressor type changes surge behavior, dynamic response, and valve sizing philosophy. | Match compressor OEM duty | Review compressor datasheet and vendor curve |  | High
Compressor data & surge basis | Process flow range | Capture minimum normal flow, maximum normal flow, startup flow, shutdown flow, and required recycle flow for every operating mode. | The valve must protect the compressor both in normal control and in upset conditions. | Full operating envelope | Study process data sheet and operating cases | In Progress
Compressor data & surge basis | Surge line | Obtain the compressor surge line from the OEM performance curve and confirm the safe operating limit. | The anti-surge system must keep the operating point away from unstable flow. | Vendor-specific | Review compressor curve and OEM documents
Compressor data & surge basis | Control line margin | Define the control line with a proper margin above the surge line based on compressor dynamics and project philosophy. | The valve must open before the compressor enters the surge region. | Typically 10–20% margin | Compare against vendor recommendation | In Progress
Compressor data & surge basis | Gas composition | Record full gas analysis including molecular weight, density, compressibility, contaminants, and any erosive or corrosive components. | Gas properties affect Cv, trim selection, erosion risk, and dynamic response. | Project specific | Review process simulation and gas analysis | Done
Compressor data & surge basis | Operating pressure | Define suction pressure, discharge pressure, and the maximum differential pressure across the recycle valve. | Differential pressure drives sizing, noise, and actuator force requirement. | Use worst-case condition | Check process conditions and upset scenarios | Not Started
Compressor data & surge basis | Operating temperature | Identify minimum, normal, and maximum gas temperature expected during all operating cases. | Temperature affects material selection, sealing, and gas density. | Project specific | Check process and upset cases | N/A
Sizing & performance | Valve capacity margin | Select a valve capacity that provides enough recycle flow with a practical safety margin. | Undersized valves cannot protect the compressor during fast surge events. | About 1.8–2.2× surge flow | Compare required flow with calculated Cv
Sizing & performance | Cv calculation basis | Perform Cv sizing using the worst credible recycle condition rather than only normal operation. | Anti-surge duty is dynamic, and upset sizing prevents failure when the compressor is stressed. | Maximum recycle demand and dp | Use sizing software or engineering calculation
Sizing & performance | Multi-scenario sizing | Check startup, normal recycle, shutdown, and upset cases together instead of relying on one emergency case only. | A valve sized for only the emergency case may behave poorly at low openings during normal operation. | All operating modes | Review all operating scenarios together
Sizing & performance | Low-flow stability | Verify that the selected valve remains stable at low openings during normal recycle duty. | Very low opening can create jetting, vibration, erosion, and oscillation. | Prefer stable opening above ~8–10% | Check expected travel during normal recycle
Sizing & performance | Emergency recycle capacity | Confirm the valve can pass the required high recycle flow quickly during a surge threat. | The compressor must be protected immediately when the operating point moves toward surge. | Must satisfy worst case recycle | Simulate upset and recycle demand
Sizing & performance | Stonewall check | Check the selected capacity against the compressor maximum flow or stonewall region. | Excessive recycle capability can create instability or push the compressor into another undesirable region. | Within compressor limits | Compare with compressor performance curve
Valve type, trim & characteristic | Valve type selection | Choose the body style that best fits capacity, pressure drop, response, and maintainability. | Body style strongly affects controllability, flow handling, and reliability. | Globe, angle, or axial flow | Review project conditions and OEM recommendation
Valve type, trim & characteristic | Globe valve suitability | Use a globe valve where throttling accuracy and stable modulation are important. | Globe valves are widely used because they provide reliable control over a broad range. | Common default choice | Evaluate rangeability and response
Valve type, trim & characteristic | Angle valve suitability | Use an angle valve where flow is high and pressure drop is severe. | Angle valves handle severe service better in some recycle applications. | High-flow / severe dp service | Review velocity and stress conditions
Valve type, trim & characteristic | Axial flow suitability | Consider an axial flow valve for high-performance compression systems requiring very fast response and high capacity. | Axial designs can provide excellent aerodynamic performance and low pressure loss. | Specialized compressor trains | Confirm vendor suitability data
Valve type, trim & characteristic | Flow characteristic | Select the flow characteristic that supports stable compressor control under dynamic conditions. | The characteristic affects loop stability and how the valve responds across its stroke. | Linear or equal % | Review control philosophy and tuning
Valve type, trim & characteristic | Linear characteristic | Prefer linear characteristic when a predictable valve position-to-flow response is needed. | Linear behavior simplifies tuning and makes response easier to understand. | Common in anti-surge duty | Compare with loop dynamics
Valve type, trim & characteristic | Equal percentage characteristic | Use equal percentage only when the operating envelope and control study justify it. | It may help in some wide-range services but is not automatically the best choice. | Case dependent | Check with control engineer and OEM
Valve type, trim & characteristic | Low-flow damage risk | Confirm that the valve will not spend long periods below a practical opening where instability or trim damage may occur. | Oversized valves can cause erosion, vibration, noise, and poor controllability. | Avoid <5% opening for long periods | Review normal recycle operating position
Valve type, trim & characteristic | Leakage class | Define the leakage class needed for shutoff performance and operating efficiency. | Excess leakage can reduce efficiency and affect control stability. | Often Class IV or better | Verify seat leakage specification
Valve type, trim & characteristic | Trim material | Select trim material for erosion, corrosion, and wear resistance under high-velocity gas service. | The trim is exposed to the harshest part of the valve service. | Special alloy if required | Review process severity and vendor data
Valve type, trim & characteristic | Anti-cavitation or special trim | Use special trim if pressure drop, velocity, or service severity demands energy dissipation. | Special trim reduces damage and improves long-term reliability. | Severe-service cases | Review vendor trim recommendation
Valve type, trim & characteristic | Multi-stage trim | Consider multi-stage trim when pressure drop is large and noise or vibration risk is high. | Splitting the pressure drop helps reduce velocity and stress on internals. | High differential pressure service | Check pressure recovery and vendor data
Actuation & accessories | Actuator type | Select an actuator that can generate the required thrust and move the valve at high speed. | Fast compressor protection depends heavily on actuator performance. | Pneumatic piston common | Check sizing and travel requirement
Actuation & accessories | Actuator action | Decide whether single-acting or double-acting operation best suits the response requirement. | Double-acting designs often provide stronger and faster control. | Double acting often preferred | Review opening and closing speed needs
Actuation & accessories | Response time | Define the total time from control signal to useful valve opening under real plant conditions. | A delay of only seconds can allow the compressor to cross into surge. | Typically 1–2 seconds or faster | Dynamic testing and stroke timing
Actuation & accessories | Stroking speed | Verify the valve can travel through the required range quickly and repeatably. | Fast stroking helps arrest surge before instability grows. | About 0.5–2 seconds | Perform stroke time test
Actuation & accessories | Fail-safe action | Specify fail-open action so the valve opens on loss of power or instrument air. | Protection must remain active during failure conditions. | Fail open is standard | Verify failure position and air supply
Actuation & accessories | Volume booster | Use a volume booster when rapid actuator air delivery is needed. | Boosters improve opening and closing speed by increasing air flow capacity. | Common fast-acting accessory | Check actuator air demand
Actuation & accessories | Quick exhaust valve | Provide quick exhaust capability when fast air release is needed. | It reduces delay during sudden valve movement. | Useful in high-speed service | Review pneumatic circuit
Actuation & accessories | Positioner type | Use a high-performance positioner suitable for fast dynamic control and accurate travel tracking. | Poor positioner response can weaken the anti-surge loop. | Smart/digital high-response type | Test step response and accuracy
Actuation & accessories | Solenoid valve | Include a solenoid valve where trip or emergency shutdown logic requires it. | The anti-surge system often depends on the solenoid for fast safety action. | Usually required by project | Check shutdown philosophy and C&E
Installation & piping | Installation location | Install the valve as close as practical to the compressor discharge to reduce dead time. | Long distances between valve and compressor slow the protective response. | Close-coupled installation preferred | Review plot plan and piping layout
Installation & piping | Recycle line volume | Keep trapped volume between the compressor and recycle valve as low as practical. | Extra volume creates response lag and reduces the effectiveness of valve movement. | Minimize line volume | Review line size, length, and routing
Installation & piping | Piping arrangement | Avoid unnecessary elbows, restrictions, dead legs, and abrupt routing changes in the recycle line. | Poor piping increases losses and response lag. | Smooth, direct routing preferred | Check piping isometrics and layout
Installation & piping | Noise control | Evaluate noise generation caused by high pressure drop and high-velocity gas flow. | Excess noise indicates severe energy loss and can damage internals or nearby equipment. | Severe-service review may be required | Perform acoustic or velocity review
Installation & piping | Vibration control | Check vibration risk in the valve, trim, piping, and supports. | Vibration can damage internals and nearby piping supports over time. | Depends on service severity | Review dynamic analysis if needed
Installation & piping | Body material | Choose body material based on gas chemistry, pressure, and temperature. | Wrong material can lead to corrosion, cracking, or premature failure. | Carbon steel, stainless steel, or alloy | Review metallurgy specification
Installation & piping | Maintenance accessibility | Confirm that the valve can be inspected, removed, and repaired without major plant disruption. | Critical equipment should be maintainable with reasonable downtime. | Project dependent | Check access space and maintenance plan
Commissioning & coordination | Dynamic testing | Verify real stroke behavior and response speed during commissioning. | A good design is not complete until tested under plant conditions. | Required before startup | Commissioning stroke and loop validation
Commissioning & coordination | Control loop tuning | Tune the anti-surge controller to match valve response and compressor dynamics. | Even a good valve will not protect properly if the loop is poorly tuned. | Project specific | Perform loop tuning and disturbance test
Commissioning & coordination | Vendor coordination | Confirm final selections with both the compressor vendor and the control valve vendor. | Protection performance depends on coordination between equipment suppliers. | Always required | Review datasheets and dynamic studies
Commissioning & coordination | Dual-valve arrangement | Consider a dual-valve arrangement where one valve handles fast emergency recycle and another handles precise low-flow control. | This can improve stability, reduce wear, and improve overall reliability in demanding systems. | Optional for complex trains | Evaluate if single valve is insufficient

## FAQ & Notes
Anti-Surge Valve Key Takeaways & FAQ
Key Takeaway | Practical Meaning
Selection is safety-critical | Anti-surge valve selection is not routine sizing; it is a compressor protection decision.
Speed matters | The valve, actuator, positioner, and accessories must work together to achieve very fast response.
System thinking is essential | Valve sizing, piping layout, compressor curve, and control tuning must be designed as one system.
FAQ | Concise Answer
How to size an anti-surge valve? | Size it for the worst credible recycle condition and include a capacity margin of about 1.8–2.2× the required surge-protection flow.
What is an anti-surge control valve? | It is a fast-acting recycle valve that maintains minimum compressor flow and prevents surge.
What are the criteria for control valve selection? | Use Cv, pressure drop, response time, valve type, actuator speed, and process conditions to guide selection.
What does an anti-surge valve do? | It opens quickly to recycle gas from discharge to suction, helping prevent flow reversal and compressor damage.
What is the difference between ATO and ATC valves? | ATO opens with air pressure and ATC closes with air pressure; anti-surge valves are typically fail-open.
What is a surge control valve? | It is another name for an anti-surge valve used to stabilize compressor operation and avoid surge.
What does anti-surge mean? | It means preventing unstable compressor flow conditions that can cause vibration, oscillation, and equipment damage.