## DCS FAT Checklist
DCS Factory Acceptance Test Checklist
Detailed checklist for documentation, hardware, software, logic, communication, redundancy, alarms, and cybersecurity verification
No | Checklist ID | Section | Checklist Item | Acceptance Criteria | Verification Method | Status | Observation / Remarks | Punch Ref | Responsible
Document Control
1 | FAT-DC-01 | Document Control | Approved Functional Design Specification available | All latest revisions signed off | Document review | Pass
2 | FAT-DC-02 | Document Control | Cause and Effect Matrix available | C&E matches approved shutdown philosophy | Document review | Pass
3 | FAT-DC-03 | Document Control | IO database frozen for FAT | Tag, range, units, and channel assignment correct | Database review | Pending
4 | FAT-DC-04 | Document Control | Alarm list approved | Priorities, deadbands, limits, and acknowledgements match philosophy | Document review | Pending
5 | FAT-DC-05 | Document Control | Graphics list and P&ID references available | Display naming and object links are consistent | Document review | Pending
6 | FAT-DC-06 | Document Control | Loop diagrams and wiring drawings available | Latest revisions reflect the installed configuration | Document review | Pending
7 | FAT-DC-07 | Document Control | Backup and restore procedure defined | Backup media and version control available | Procedure review | Pending
Hardware and Cabinet Inspection
8 | FAT-HW-01 | Hardware and Cabinet Inspection | Cabinet quantity and tag check | All panels match GA drawings and nameplates | Visual inspection | Pending
9 | FAT-HW-02 | Hardware and Cabinet Inspection | Cabinet physical condition check | No transport damage, dents, rust, or panel distortion | Visual inspection | Pending
10 | FAT-HW-03 | Hardware and Cabinet Inspection | Door, lock, hinge, and gasket check | Doors open smoothly and close properly | Mechanical inspection | Pending
11 | FAT-HW-04 | Hardware and Cabinet Inspection | Ventilation and cooling fan check | Airflow direction and fan operation are correct | Functional inspection | Pending
12 | FAT-HW-05 | Hardware and Cabinet Inspection | Terminal labeling verification | All terminals and wires match drawings | Visual inspection | Pending
13 | FAT-HW-06 | Hardware and Cabinet Inspection | Ferrule and crimp quality check | Crimps are firm, readable, and consistent | Visual inspection | Pending
14 | FAT-HW-07 | Hardware and Cabinet Inspection | Cable dressing and segregation | Signal, power, and communication cables are separated | Visual inspection | Pending
15 | FAT-HW-08 | Hardware and Cabinet Inspection | Earthing and shielding arrangement | Shield termination and earth bus arrangement comply | Visual inspection | Pending
16 | FAT-HW-09 | Hardware and Cabinet Inspection | Hardware BOM cross check | Installed modules match approved BOM | Document cross-check | Pending
Power and Startup Verification
17 | FAT-PWR-01 | Power and Startup Verification | UPS input/output verification | Voltage within acceptable limits and alarms normal | Measurement | Pending
18 | FAT-PWR-02 | Power and Startup Verification | Redundant power supply check | Either supply can support the load without interruption | Switchover test | Pending
19 | FAT-PWR-03 | Power and Startup Verification | DC distribution verification | Correct polarity and fuse ratings confirmed | Measurement | Pending
20 | FAT-PWR-04 | Power and Startup Verification | Sequential power-up validation | UPS, switches, controllers, servers, and workstations start correctly | Startup observation | Pending
21 | FAT-PWR-05 | Power and Startup Verification | Voltage stability monitoring | No abnormal drop, ripple, or spike observed | Trend observation | Pending
22 | FAT-PWR-06 | Power and Startup Verification | System boot diagnostics | No critical boot errors or startup faults | Functional check | Pending
Controller and Server Testing
23 | FAT-CTL-01 | Controller and Server Testing | CPU health verification | Processor diagnostics normal and memory healthy | Diagnostic check | Pending
24 | FAT-CTL-02 | Controller and Server Testing | Controller synchronization | Primary and standby controllers remain synchronized | Switchover test | Pending
25 | FAT-CTL-03 | Controller and Server Testing | Controller redundancy switchover | Live transfer occurs without disturbing control loops | Live failover test | Pending
26 | FAT-CTL-04 | Controller and Server Testing | Scan time verification | Cycle time remains within acceptable limits | Performance test | Pending
27 | FAT-CTL-05 | Controller and Server Testing | CPU loading verification | CPU utilization remains within project limit | Performance monitoring | Pending
28 | FAT-CTL-06 | Controller and Server Testing | Server startup and services | Application, historian, and alarm services start correctly | Functional check | Pending
29 | FAT-CTL-07 | Controller and Server Testing | Operator workstation health | Graphics, trends, faceplates, and login function properly | Functional check | Pending
30 | FAT-CTL-08 | Controller and Server Testing | Time synchronization | All nodes show the same time source | Verification | Pending
IO Loop Testing
31 | FAT-IO-01 | IO Loop Testing | Analog input scaling | 0 to 100 percent and engineering units are correct | Signal simulation | Pending
32 | FAT-IO-02 | IO Loop Testing | Analog input alarm limits | HH, H, L, LL alarms act at approved setpoints | Signal simulation | Pending
33 | FAT-IO-03 | IO Loop Testing | Analog output tracking | Output follows command correctly across full range | Signal simulation | Pending
34 | FAT-IO-04 | IO Loop Testing | Digital input status | ON/OFF state is read correctly by DCS | Contact simulation | Pending
35 | FAT-IO-05 | IO Loop Testing | Digital output command | Output energizes the correct device and feedback is correct | Command simulation | Pending
36 | FAT-IO-06 | IO Loop Testing | RTD input verification | Temperature indication is stable and scaled correctly | Signal simulation | Pending
37 | FAT-IO-07 | IO Loop Testing | Thermocouple input verification | Polarity, range, and indication are correct | Signal simulation | Pending
38 | FAT-IO-08 | IO Loop Testing | Pulse input verification | Pulse count and rate are computed correctly | Signal simulation | Pending
39 | FAT-IO-09 | IO Loop Testing | IO channel cross mapping check | Tag displayed matches simulated channel | Database review | Pending
Logic, Cause and Effect, and Shutdown
40 | FAT-LOG-01 | Logic, Cause and Effect, and Shutdown | Cause and effect testing | Every cause produces the expected trip or action | Logic simulation | Pending
41 | FAT-LOG-02 | Logic, Cause and Effect, and Shutdown | Permissive logic testing | Start command enabled only when permissives are satisfied | Logic simulation | Pending
42 | FAT-LOG-03 | Logic, Cause and Effect, and Shutdown | Trip logic verification | Trip actions occur in the correct sequence and timing | Logic simulation | Pending
43 | FAT-LOG-04 | Logic, Cause and Effect, and Shutdown | Bypass and override testing | Authorized bypass behavior is controlled and logged | Logic simulation | Pending
44 | FAT-LOG-05 | Logic, Cause and Effect, and Shutdown | Sequence logic verification | Start-up and shutdown sequence steps execute correctly | Logic simulation | Pending
45 | FAT-LOG-06 | Logic, Cause and Effect, and Shutdown | Fail safe action verification | Devices move to approved safe state on failure | Failure simulation | Pending
HMI, Alarms, and Trends
46 | FAT-HMI-01 | HMI, Alarms, and Trends | Mimic display accuracy | Equipment, tags, and process values are displayed correctly | Visual inspection | Pending
47 | FAT-HMI-02 | HMI, Alarms, and Trends | Faceplate operation | Faceplates open, command, and display status correctly | Operator interaction | Pending
48 | FAT-HMI-03 | HMI, Alarms, and Trends | Navigation and menu structure | Screen movement is clear and intuitive | Operator review | Pending
49 | FAT-HMI-04 | HMI, Alarms, and Trends | Trend display verification | Live and historical trends show correct data | Functional check | Pending
50 | FAT-HMI-05 | HMI, Alarms, and Trends | Alarm banner and annunciation | Priorities and colors behave according to philosophy | Functional check | Pending
51 | FAT-HMI-06 | HMI, Alarms, and Trends | Historical event logging | Alarm and event timestamps are captured correctly | Database check | Pending
52 | FAT-HMI-07 | HMI, Alarms, and Trends | Color consistency and object animation | Valve, motor, and status colors follow standards | Visual inspection | Pending
Communication and Integration
53 | FAT-COM-01 | Communication and Integration | Modbus TCP communication | Registers, timeouts, and data order are correct | Protocol test | Pending
54 | FAT-COM-02 | Communication and Integration | Modbus RTU communication | Serial settings and register mapping are correct | Protocol test | Pending
55 | FAT-COM-03 | Communication and Integration | OPC communication | Read/write tags transfer correctly | Protocol test | Pending
56 | FAT-COM-04 | Communication and Integration | Profibus / fieldbus interface | Addressing and diagnostics are correct | Network test | Pending
57 | FAT-COM-05 | Communication and Integration | Ethernet gateway and routing | No duplicate IP and no routing conflict | Network test | Pending
58 | FAT-COM-06 | Communication and Integration | Third-party interface simulation | Data exchange behaves as per the integration list | Integration test | Pending
Redundancy, Backup, Cybersecurity
59 | FAT-SEC-01 | Redundancy, Backup, Cybersecurity | Server redundancy test | Standby server takes over correctly | Failover test | Pending
60 | FAT-SEC-02 | Redundancy, Backup, Cybersecurity | Network redundancy test | Switch or ring failure does not stop communication | Failover test | Pending
61 | FAT-SEC-03 | Redundancy, Backup, Cybersecurity | Power redundancy test | Loss of one PSU does not affect operation | Failover test | Pending
62 | FAT-SEC-04 | Redundancy, Backup, Cybersecurity | Backup creation | Controller and server backups created successfully | Backup procedure | Pending
63 | FAT-SEC-05 | Redundancy, Backup, Cybersecurity | Restore validation | Backup can be restored without configuration loss | Restore test | Pending
64 | FAT-SEC-06 | Redundancy, Backup, Cybersecurity | User access levels | Operator, engineer, and admin rights are correct | Access review | Pending
65 | FAT-SEC-07 | Redundancy, Backup, Cybersecurity | Password policy and USB control | Security restrictions are active | Policy review | Pending

## Summary
DCS FAT Checklist Summary
Metric | Value | Progress Overview
Total Checklist Items | 65 | Completion | 3.077%
Pass | 2 | Total Items | 65
Fail | 0 | Open Issues | 0
Pending | 63
Not Applicable | 0
Completion % | 3.077%

## Instructions
How to Use This Workbook
Guidance
Open the DCS FAT Checklist sheet and review each section in sequence.
Use the Status dropdown to mark each item as Pending, Pass, Fail, or NA.
Write observations, punch items, and notes in the Remarks column.
Use the Summary sheet to monitor overall completion and open issues.
Print the workbook in landscape layout for witness FAT sessions.
Suggested review order: Document Control → Hardware → Power → Controllers → IO → Logic → HMI → Communication → Security.