## Dashboard
Safety Instrumented System (SIS) Running Inspection Checklist
IEC 61511 • Functional Safety • Plant Inspection • Running Checklist Dashboard
Total Items |  | Daily Items |  | Weekly Items | Monthly Items | Quarterly Items | Annual Items | Open Issues
70 |  | 17 |  | 18 | 21 | 12 | 1 | 0
Closed Issues
0
Frequency Summary |  |  | Section Summary
Frequency | Item Count |  | Section | Item Count
Daily | 17 |  | Section A - SIS Health | 10
Weekly | 18 |  | Section B - PLC Solver | 10
Monthly | 21 |  | Section C - Field Instruments | 10
Quarterly | 12 |  | Section D - Final Elements | 10
Annual | 1 |  | Section E - Bypass Mgmt | 5
Shutdown / Turnaround | 1 |  | Section F - UPS Power | 5
|  |  | Section G - Network | 5
|  |  | Section H - Panel Env | 5
|  |  | Section I - Compliance | 5
|  |  | Section J - Ops Practice | 5

## Master Checklist
Safety Instrumented System (SIS) Running Inspection Checklist
Master checklist for SIS, safety PLC, field instruments, final elements, bypass management, UPS, network, and IEC 61511 compliance inspections.
Sl No | Section | Inspection Area | Equipment / Tag | Inspection Requirement | Expected Condition | Inspection Method | Frequency | Status | Remarks | Responsible Person | Date Checked | Next Due Date | Priority | Action Required
1 | Section A - SIS Health | SIS Controller | Safety PLC | Controller healthy status | Healthy without fault | HMI diagnostics | Daily | [5 empty] | Critical
2 | Section A - SIS Health | CPU Redundancy | Redundant CPU | Redundant synchronization | Both CPUs synchronized | PLC diagnostics | Daily | [5 empty] | Critical
3 | Section A - SIS Health | Power Supply | SIS Power Module | Voltage monitoring | Stable DC voltage | Multimeter / HMI | Daily | [5 empty] | High
4 | Section A - SIS Health | Communication | Safety Network | Communication integrity | No communication loss | Diagnostic screen | Daily | [5 empty] | High
5 | Section A - SIS Health | SOE System | Event Recorder | Time synchronization | Accurate timestamp | SOE check | Weekly | [5 empty] | Medium
6 | Section A - SIS Health | Diagnostics | SIS Alarms | Diagnostic alarm review | No critical alarms | Alarm review | Daily | [5 empty] | High
7 | Section A - SIS Health | Memory Utilization | PLC Memory | Memory load verification | Within safe limit | Engineering station | Monthly | [5 empty] | Medium
8 | Section A - SIS Health | Redundancy | CPU Switchover | Switchover readiness | Successful redundancy | Diagnostic review | Monthly | [5 empty] | Critical
9 | Section A - SIS Health | Application Integrity | Safety Logic | Checksum verification | Matching checksum | Engineering software | Monthly | [5 empty] | Critical
10 | Section A - SIS Health | Cybersecurity | SIS Access | Unauthorized access check | No unauthorized login | Audit logs | Weekly | [5 empty] | High
11 | Section B - PLC Solver | CPU Diagnostics | Safety PLC CPU | CPU fault monitoring | No active fault | HMI diagnostics | Daily | [5 empty] | Critical
12 | Section B - PLC Solver | Scan Time | Logic Solver | Scan time verification | Within design limit | Diagnostic tools | Weekly | [5 empty] | High
13 | Section B - PLC Solver | Communication | Redundant Ethernet | Communication redundancy | Healthy redundancy | Switch diagnostics | Weekly | [5 empty] | High
14 | Section B - PLC Solver | Logic Validation | Safety Program | Logic mismatch verification | No mismatch | Compare tool | Monthly | [5 empty] | Critical
15 | Section B - PLC Solver | Fault LEDs | PLC Rack | LED fault inspection | No red LEDs | Visual inspection | Daily | [5 empty] | High
16 | Section B - PLC Solver | Bypass Monitoring | Safety Logic | Active bypass check | No unauthorized bypass | Bypass report | Daily | [5 empty] | Critical
17 | Section B - PLC Solver | Forced I/O | Safety PLC | Forced signal verification | No active force | Engineering station | Daily | [5 empty] | Critical
18 | Section B - PLC Solver | Firmware | PLC Firmware | Firmware verification | Approved version | Software check | Quarterly | [5 empty] | Medium
19 | Section B - PLC Solver | Online Edits | SIS Logic | Unauthorized online edit check | No unauthorized changes | Audit review | Weekly | [5 empty] | Critical
20 | Section B - PLC Solver | Battery Health | CPU Battery | Battery voltage check | Healthy battery | Diagnostics | Monthly | [5 empty] | Medium
21 | Section C - Field Instruments | Pressure Transmitter | PT-101 | Calibration status | Within calibration validity | Calibration record | Monthly | [5 empty] | High
22 | Section C - Field Instruments | Temperature Transmitter | TT-101 | Sensor drift check | Stable reading | Trend analysis | Monthly | [5 empty] | Medium
23 | Section C - Field Instruments | Flow Transmitter | FT-201 | Impulse line leakage | No leakage | Visual inspection | Weekly | [5 empty] | Medium
24 | Section C - Field Instruments | Level Transmitter | LT-301 | Diagnostic health | Healthy diagnostics | HART communicator | Weekly | [5 empty] | High
25 | Section C - Field Instruments | Gas Detector | GD-101 | Sensor poisoning check | Normal sensor response | Gas bump test | Monthly | [5 empty] | Critical
26 | Section C - Field Instruments | Flame Detector | FD-201 | Optical cleanliness | Lens clean | Visual inspection | Weekly | [5 empty] | High
27 | Section C - Field Instruments | Vibration Switch | VS-101 | Mechanical integrity | Secure mounting | Physical check | Monthly | [5 empty] | Medium
28 | Section C - Field Instruments | ESD Push Button | PB-ESD-01 | Functional verification | Operable condition | Functional test | Monthly | [5 empty] | Critical
29 | Section C - Field Instruments | Limit Switch | LSH-101 | Switching integrity | Proper operation | Simulation test | Quarterly | [5 empty] | Medium
30 | Section C - Field Instruments | Junction Box | JB-SIS-01 | Water ingress check | Dry and sealed | Visual inspection | Monthly | [5 empty] | High
31 | Section D - Final Elements | Shutdown Valve | XV-101 | Partial stroke testing | Smooth movement | PST system | Monthly | [5 empty] | Critical
32 | Section D - Final Elements | ESD Valve | SDV-201 | Leakage verification | No passing leakage | Leak test | Quarterly | [5 empty] | Critical
33 | Section D - Final Elements | Solenoid Valve | SOV-101 | Coil resistance check | Normal resistance | Multimeter | Monthly | [5 empty] | Critical
34 | Section D - Final Elements | MOV | MOV-401 | Position feedback | Accurate indication | Functional test | Monthly | [5 empty] | High
35 | Section D - Final Elements | Pneumatic Supply | Air Header | Air pressure monitoring | Stable pressure | Pressure gauge | Daily | [5 empty] | Critical
36 | Section D - Final Elements | Valve Stroke | SDV-202 | Stroke timing | Within design limit | Stroke timer | Quarterly | [5 empty] | Critical
37 | Section D - Final Elements | Fail Safe Action | Shutdown Valve | Fail-safe verification | Correct fail position | Functional test | Shutdown / Turnaround | [5 empty] | Critical
38 | Section D - Final Elements | Mechanical Integrity | Valve Assembly | Obstruction check | No obstruction | Visual inspection | Monthly | [5 empty] | High
39 | Section D - Final Elements | Positioner Feedback | Valve Positioner | Signal response | Stable response | Loop test | Quarterly | [5 empty] | High
40 | Section D - Final Elements | Bypass Valve | Manual Bypass | Position verification | Closed and locked | Visual inspection | Daily | [5 empty] | Critical
41 | Section E - Bypass Mgmt | Bypass Monitoring | SIS Bypass | Active bypass review | Authorized only | Bypass log review | Daily | [5 empty] | Critical
42 | Section E - Bypass Mgmt | Override Management | Temporary Override | Timeout verification | Within approved limit | Override report | Daily | [5 empty] | High
43 | Section E - Bypass Mgmt | Alarm Management | Alarm System | Alarm shelving review | No stale shelving | Alarm review | Daily | [5 empty] | High
44 | Section E - Bypass Mgmt | Alarm Flood | Operator Station | Alarm flood analysis | Controlled alarm rate | Alarm analytics | Weekly | [5 empty] | Medium
45 | Section E - Bypass Mgmt | Key Control | Bypass Key | Key management verification | Controlled access | Audit check | Weekly | [5 empty] | High
46 | Section F - UPS Power | UPS Health | UPS Panel | UPS status monitoring | Healthy operation | HMI / UPS panel | Daily | [5 empty] | Critical
47 | Section F - UPS Power | Battery Voltage | UPS Battery | Battery condition | Stable voltage | Battery tester | Monthly | [5 empty] | Critical
48 | Section F - UPS Power | Charger Health | Charger Unit | Charger verification | Normal charging | Indicator check | Weekly | [5 empty] | High
49 | Section F - UPS Power | Earthing | SIS Panel | Earthing continuity | Low resistance | Earth tester | Quarterly | [5 empty] | Critical
50 | Section F - UPS Power | Panel Temperature | SIS Cabinet | Temperature monitoring | Normal temperature | Thermal scanner | Weekly | [5 empty] | High
51 | Section G - Network | Safety Network | SIS Ethernet | Communication stability | No packet loss | Diagnostics | Weekly | [5 empty] | High
52 | Section G - Network | Fiber Link | Fiber Network | Fiber health verification | Healthy link | OTDR / diagnostics | Quarterly | [5 empty] | High
53 | Section G - Network | Switch Health | Network Switch | Port diagnostics | No failed ports | Switch monitoring | Weekly | [5 empty] | High
54 | Section G - Network | Firewall | SIS Firewall | Security monitoring | No unauthorized event | Security logs | Weekly | [5 empty] | Critical
55 | Section G - Network | Network Latency | SIS Communication | Latency monitoring | Within limit | Monitoring software | Monthly | [5 empty] | Medium
56 | Section H - Panel Env | Panel Cleanliness | SIS Cabinet | Dust inspection | Clean condition | Visual inspection | Weekly | [5 empty] | Medium
57 | Section H - Panel Env | Cooling Fan | Panel Fan | Fan operation | Proper airflow | Physical inspection | Monthly | [5 empty] | High
58 | Section H - Panel Env | HVAC | Instrument Room | HVAC condition | Stable temperature | HVAC check | Weekly | [5 empty] | High
59 | Section H - Panel Env | Water Ingress | Panel Door | Seal inspection | No ingress | Visual inspection | Monthly | [5 empty] | Critical
60 | Section H - Panel Env | Corrosion | Terminal Blocks | Corrosion inspection | No corrosion | Visual inspection | Quarterly | [5 empty] | High
61 | Section I - Compliance | SIL Records | SIS Documentation | SIL verification review | Updated records | Document audit | Quarterly | [5 empty] | High
62 | Section I - Compliance | Proof Test | SIF Loop | Proof test due review | No overdue tests | Maintenance records | Monthly | [5 empty] | Critical
63 | Section I - Compliance | Cause and Effect | Shutdown Matrix | Logic validation | Accurate sequence | Review / test | Quarterly | [5 empty] | Critical
64 | Section I - Compliance | SRS | Safety Requirement Spec | SRS availability | Approved copy available | Document review | Quarterly | [5 empty] | High
65 | Section I - Compliance | Lifecycle Documents | SIS System | Documentation completeness | Updated lifecycle records | Audit | Annual | [5 empty] | Medium
66 | Section J - Ops Practice | Bypass Logbook | Shift Records | Logbook review | Updated entries | Document review | Daily | [5 empty] | High
67 | Section J - Ops Practice | Shift Handover | Operations | Safety communication | Complete communication | Interview / review | Daily | [5 empty] | High
68 | Section J - Ops Practice | Operator Awareness | Operations Team | SIS awareness check | Adequate knowledge | Interview | Monthly | [5 empty] | Medium
69 | Section J - Ops Practice | PTW Compliance | Maintenance Work | Permit verification | Proper permit usage | Audit | Weekly | [5 empty] | High
70 | Section J - Ops Practice | Emergency Preparedness | Operations Team | Emergency readiness | Prepared personnel | Drill review | Quarterly | [5 empty] | Critical

## Lists
Status | Priority | Frequency
OK | Low | Daily
Passed | Medium | Weekly
Attention | High | Monthly
Warning | Critical | Quarterly
Failed |  | Annual
Critical |  | Shutdown / Turnaround
Completed
Closed
Not Applicable

## Section A - SIS Health
Section A – SIS Health
Section-specific SIS running inspection checklist with filters, dropdowns, and next-due-date logic.
Sl No | Inspection Area | Equipment / Tag | Inspection Requirement | Expected Condition | Inspection Method | Frequency | Status | Remarks | Date Checked | Next Due Date
1 | Safety PLC | Controller healthy status | Healthy without fault | HMI diagnostics | Daily | Critical
2 | Redundant CPU | Redundant synchronization | Both CPUs synchronized | PLC diagnostics | Daily | Critical
3 | SIS Power Module | Voltage monitoring | Stable DC voltage | Multimeter / HMI | Daily | High
4 | Safety Network | Communication integrity | No communication loss | Diagnostic screen | Daily | High
5 | Event Recorder | Time synchronization | Accurate timestamp | SOE check | Weekly | Medium
6 | SIS Alarms | Diagnostic alarm review | No critical alarms | Alarm review | Daily | High
7 | PLC Memory | Memory load verification | Within safe limit | Engineering station | Monthly | Medium
8 | CPU Switchover | Switchover readiness | Successful redundancy | Diagnostic review | Monthly | Critical
9 | Safety Logic | Checksum verification | Matching checksum | Engineering software | Monthly | Critical
10 | SIS Access | Unauthorized access check | No unauthorized login | Audit logs | Weekly | High

## Section B - PLC Solver
Section B – PLC Solver
Section-specific SIS running inspection checklist with filters, dropdowns, and next-due-date logic.
Sl No | Inspection Area | Equipment / Tag | Inspection Requirement | Expected Condition | Inspection Method | Frequency | Status | Remarks | Date Checked | Next Due Date
11 | Safety PLC CPU | CPU fault monitoring | No active fault | HMI diagnostics | Daily | Critical
12 | Logic Solver | Scan time verification | Within design limit | Diagnostic tools | Weekly | High
13 | Redundant Ethernet | Communication redundancy | Healthy redundancy | Switch diagnostics | Weekly | High
14 | Safety Program | Logic mismatch verification | No mismatch | Compare tool | Monthly | Critical
15 | PLC Rack | LED fault inspection | No red LEDs | Visual inspection | Daily | High
16 | Safety Logic | Active bypass check | No unauthorized bypass | Bypass report | Daily | Critical
17 | Safety PLC | Forced signal verification | No active force | Engineering station | Daily | Critical
18 | PLC Firmware | Firmware verification | Approved version | Software check | Quarterly | Medium
19 | SIS Logic | Unauthorized online edit check | No unauthorized changes | Audit review | Weekly | Critical
20 | CPU Battery | Battery voltage check | Healthy battery | Diagnostics | Monthly | Medium

## Section C - Field Instruments
Section C – Field Instruments
Section-specific SIS running inspection checklist with filters, dropdowns, and next-due-date logic.
Sl No | Inspection Area | Equipment / Tag | Inspection Requirement | Expected Condition | Inspection Method | Frequency | Status | Remarks | Date Checked | Next Due Date
21 | PT-101 | Calibration status | Within calibration validity | Calibration record | Monthly | High
22 | TT-101 | Sensor drift check | Stable reading | Trend analysis | Monthly | Medium
23 | FT-201 | Impulse line leakage | No leakage | Visual inspection | Weekly | Medium
24 | LT-301 | Diagnostic health | Healthy diagnostics | HART communicator | Weekly | High
25 | GD-101 | Sensor poisoning check | Normal sensor response | Gas bump test | Monthly | Critical
26 | FD-201 | Optical cleanliness | Lens clean | Visual inspection | Weekly | High
27 | VS-101 | Mechanical integrity | Secure mounting | Physical check | Monthly | Medium
28 | PB-ESD-01 | Functional verification | Operable condition | Functional test | Monthly | Critical
29 | LSH-101 | Switching integrity | Proper operation | Simulation test | Quarterly | Medium
30 | JB-SIS-01 | Water ingress check | Dry and sealed | Visual inspection | Monthly | High

## Section D - Final Elements
Section D – Final Elements
Section-specific SIS running inspection checklist with filters, dropdowns, and next-due-date logic.
Sl No | Inspection Area | Equipment / Tag | Inspection Requirement | Expected Condition | Inspection Method | Frequency | Status | Remarks | Date Checked | Next Due Date
31 | XV-101 | Partial stroke testing | Smooth movement | PST system | Monthly | Critical
32 | SDV-201 | Leakage verification | No passing leakage | Leak test | Quarterly | Critical
33 | SOV-101 | Coil resistance check | Normal resistance | Multimeter | Monthly | Critical
34 | MOV-401 | Position feedback | Accurate indication | Functional test | Monthly | High
35 | Air Header | Air pressure monitoring | Stable pressure | Pressure gauge | Daily | Critical
36 | SDV-202 | Stroke timing | Within design limit | Stroke timer | Quarterly | Critical
37 | Shutdown Valve | Fail-safe verification | Correct fail position | Functional test | Shutdown / Turnaround | Critical
38 | Valve Assembly | Obstruction check | No obstruction | Visual inspection | Monthly | High
39 | Valve Positioner | Signal response | Stable response | Loop test | Quarterly | High
40 | Manual Bypass | Position verification | Closed and locked | Visual inspection | Daily | Critical

## Section E - Bypass Mgmt
Section E – Bypass Mgmt
Section-specific SIS running inspection checklist with filters, dropdowns, and next-due-date logic.
Sl No | Inspection Area | Equipment / Tag | Inspection Requirement | Expected Condition | Inspection Method | Frequency | Status | Remarks | Date Checked | Next Due Date
41 | SIS Bypass | Active bypass review | Authorized only | Bypass log review | Daily | Critical
42 | Temporary Override | Timeout verification | Within approved limit | Override report | Daily | High
43 | Alarm System | Alarm shelving review | No stale shelving | Alarm review | Daily | High
44 | Operator Station | Alarm flood analysis | Controlled alarm rate | Alarm analytics | Weekly | Medium
45 | Bypass Key | Key management verification | Controlled access | Audit check | Weekly | High

## Section F - UPS Power
Section F – UPS Power
Section-specific SIS running inspection checklist with filters, dropdowns, and next-due-date logic.
Sl No | Inspection Area | Equipment / Tag | Inspection Requirement | Expected Condition | Inspection Method | Frequency | Status | Remarks | Date Checked | Next Due Date
46 | UPS Panel | UPS status monitoring | Healthy operation | HMI / UPS panel | Daily | Critical
47 | UPS Battery | Battery condition | Stable voltage | Battery tester | Monthly | Critical
48 | Charger Unit | Charger verification | Normal charging | Indicator check | Weekly | High
49 | SIS Panel | Earthing continuity | Low resistance | Earth tester | Quarterly | Critical
50 | SIS Cabinet | Temperature monitoring | Normal temperature | Thermal scanner | Weekly | High

## Section G - Network
Section G – Network
Section-specific SIS running inspection checklist with filters, dropdowns, and next-due-date logic.
Sl No | Inspection Area | Equipment / Tag | Inspection Requirement | Expected Condition | Inspection Method | Frequency | Status | Remarks | Date Checked | Next Due Date
51 | SIS Ethernet | Communication stability | No packet loss | Diagnostics | Weekly | High
52 | Fiber Network | Fiber health verification | Healthy link | OTDR / diagnostics | Quarterly | High
53 | Network Switch | Port diagnostics | No failed ports | Switch monitoring | Weekly | High
54 | SIS Firewall | Security monitoring | No unauthorized event | Security logs | Weekly | Critical
55 | SIS Communication | Latency monitoring | Within limit | Monitoring software | Monthly | Medium

## Section H - Panel Env
Section H – Panel Env
Section-specific SIS running inspection checklist with filters, dropdowns, and next-due-date logic.
Sl No | Inspection Area | Equipment / Tag | Inspection Requirement | Expected Condition | Inspection Method | Frequency | Status | Remarks | Date Checked | Next Due Date
56 | SIS Cabinet | Dust inspection | Clean condition | Visual inspection | Weekly | Medium
57 | Panel Fan | Fan operation | Proper airflow | Physical inspection | Monthly | High
58 | Instrument Room | HVAC condition | Stable temperature | HVAC check | Weekly | High
59 | Panel Door | Seal inspection | No ingress | Visual inspection | Monthly | Critical
60 | Terminal Blocks | Corrosion inspection | No corrosion | Visual inspection | Quarterly | High

## Section I - Compliance
Section I – Compliance
Section-specific SIS running inspection checklist with filters, dropdowns, and next-due-date logic.
Sl No | Inspection Area | Equipment / Tag | Inspection Requirement | Expected Condition | Inspection Method | Frequency | Status | Remarks | Date Checked | Next Due Date
61 | SIS Documentation | SIL verification review | Updated records | Document audit | Quarterly | High
62 | SIF Loop | Proof test due review | No overdue tests | Maintenance records | Monthly | Critical
63 | Shutdown Matrix | Logic validation | Accurate sequence | Review / test | Quarterly | Critical
64 | Safety Requirement Spec | SRS availability | Approved copy available | Document review | Quarterly | High
65 | SIS System | Documentation completeness | Updated lifecycle records | Audit | Annual | Medium

## Section J - Ops Practice
Section J – Ops Practice
Section-specific SIS running inspection checklist with filters, dropdowns, and next-due-date logic.
Sl No | Inspection Area | Equipment / Tag | Inspection Requirement | Expected Condition | Inspection Method | Frequency | Status | Remarks | Date Checked | Next Due Date
66 | Shift Records | Logbook review | Updated entries | Document review | Daily | High
67 | Operations | Safety communication | Complete communication | Interview / review | Daily | High
68 | Operations Team | SIS awareness check | Adequate knowledge | Interview | Monthly | Medium
69 | Maintenance Work | Permit verification | Proper permit usage | Audit | Weekly | High
70 | Operations Team | Emergency readiness | Prepared personnel | Drill review | Quarterly | Critical

## Corrective Actions
SIS Troubleshooting and Corrective Actions
Common SIS failures, probable causes, and practical corrective actions for plant maintenance and operations.
Issue | Symptom | Root Cause | Impact | Corrective Action | Priority | Owner | Target Date | Status
Frequent false trips | Ground loop or signal noise | Verify shielding and grounding | Production upset | Verify grounding and wiring | High | Instrument / I&C |  | Open
Valve sluggish movement | Corrosion or air leakage | Perform maintenance and PST | Delayed shutdown response | Inspect actuator, tubing, and valve | Critical | Mechanical |  | Open
Sensor drift | Aging transmitter sensor | Recalibrate or replace sensor | Unsafe process operation | Recalibrate or replace | High | Instrumentation |  | Open
CPU redundancy mismatch | Firmware inconsistency | Synchronize firmware | Reduced availability | Align firmware versions | Critical | Automation |  | Open
Water ingress in JB | Failed gland sealing | Replace cable gland | Corrosion / signal loss | Replace seals and dry terminals | High | Maintenance |  | Open
Gas detector unstable | Sensor poisoning | Replace sensing element | Gas leak undetected | Replace sensor and retest | Critical | Safety |  | Open
High panel temperature | HVAC failure | Restore cooling immediately | Electronics damage | Repair cooling and monitor | High | Electrical |  | Open
Communication alarm | Fiber issue | Inspect switch and fiber link | SIS communication loss | Inspect links and switches | Critical | Network |  | Open
UPS alarm | Battery degradation | Replace battery set | Power interruption | Replace batteries and verify charger | Critical | Electrical |  | Open
Bypass left active | Operator oversight | Review and remove bypass | Safety function disabled | Remove bypass and retrain | Critical | Operations |  | Open

## Frequency Summary
Inspection Frequency Summary
Frequency counts and section roll-up for the SIS running inspection checklist.
Frequency | Item Count | Share %
Daily | 17 | 24.29%
Weekly | 18 | 25.71%
Monthly | 21 | 30%
Quarterly | 12 | 17.14%
Annual | 1 | 1.429%
Shutdown / Turnaround | 1 | 1.429%
Total | 70 | 100%
Section | Item Count
Section A - SIS Health | 10
Section B - PLC Solver | 10
Section C - Field Instruments | 10
Section D - Final Elements | 10
Section E - Bypass Mgmt | 5
Section F - UPS Power | 5
Section G - Network | 5
Section H - Panel Env | 5
Section I - Compliance | 5
Section J - Ops Practice | 5