## Checklist
Advanced Instrumentation Failure Prevention Checklist for Process Plants
ID | Category | Checklist Item | Failure Sign | Root Cause Focus | Priority | Status | Risk Score | Corrective Action | Preventive Action | Owner | Remarks
CHK-001 | Installation | Verify transmitter mounting orientation and accessibility | Unstable reading or difficult maintenance | Wrong mounting or poor access | High | Open | 3 | Check mounting and accessibility | Use correct installation drawings and maintain service access
CHK-002 | Installation | Check impulse line slope and equal length | False level or slow response | Condensate trap or trapped gas | High | Open | 3 | Rework impulse line routing | Keep impulse lines short, equal, and properly sloped
CHK-003 | Installation | Confirm supports for tubing and cable | Loose fittings or vibration damage | Unsupported tubing | High | Open | 3 | Add supports and clamps | Inspect supports during commissioning and PM
CHK-004 | Environment | Inspect enclosure sealing and cable glands | Moisture inside box or signal loss | Water ingress | High | Open | 3 | Replace glands and damaged seals | Use correct IP rating and inspect before rainy season
CHK-005 | Environment | Check corrosion on terminals and covers | Intermittent open circuit | Humidity and corrosion | High | Open | 3 | Clean and replace affected parts | Apply anti corrosion protection and regular inspection
CHK-006 | Environment | Verify enclosure suitability for outdoor or washdown area | Display failure or terminal damage | Wrong enclosure protection | Medium | Open | 2 | Upgrade enclosure protection | Match IP rating to actual site condition
CHK-007 | Vibration | Inspect instruments near pumps and compressors | Frequent early failure | Mechanical vibration | High | Open | 3 | Relocate or isolate instrument | Use vibration resistant mounting and better support
CHK-008 | Vibration | Check gauge needles and brackets for pulsation damage | Unstable indication | Process pulsation | Medium | Open | 2 | Install snubber or damper | Reduce pulsation at source where possible
CHK-009 | Vibration | Look for loose fittings and cracked tubing | Repeated leak or drift | Mechanical fatigue | High | Open | 3 | Replace damaged parts | Include vibration checks in PM rounds
CHK-010 | Calibration | Compare as found and as left values | Reading is stable but wrong | Calibration drift | High | Open | 3 | Recalibrate and trend results | Set calibration interval by risk and history
CHK-011 | Calibration | Review drift history for critical loops | Repeated offset on calibration | Sensor aging | High | Open | 3 | Shorten calibration interval | Track drift trends during reliability review
CHK-012 | Calibration | Verify temperature and process influence on sensors | Slow deviation over months | Thermal cycling | Medium | Open | 2 | Correct environmental cause | Use correct sensor and service rating
CHK-013 | Electrical | Check loop continuity and signal wiring | Noisy or unstable output | Loose or damaged wiring | High | Open | 3 | Repair wiring and terminals | Use proper loop checking before startup
CHK-014 | Electrical | Verify grounding and shield termination | Random spikes or signal noise | Poor grounding | High | Open | 3 | Correct earthing and shielding | Keep signal and power cables separated
CHK-015 | Electrical | Inspect junction box and terminal tightness | Intermittent signal loss | Poor terminal contact | Medium | Open | 2 | Tighten and replace terminals | Include terminal inspection in PM
CHK-016 | Process | Inspect impulse lines for sludge or blockage | False level or slow response | Process plugging | High | Open | 3 | Clean and flush lines | Design for dirty service access
CHK-017 | Process | Check for scaling and fouling on wetted parts | Wrong measurement or slow response | Buildup or contamination | High | Open | 3 | Clean wetted parts and verify service | Plan maintenance for dirty or slurry service
CHK-018 | Process | Review whether material selection suits the process | Early corrosion or repeat failure | Wrong material compatibility | High | Open | 3 | Replace with compatible material | Confirm process chemistry before selection
CHK-019 | Selection | Check pressure range and temperature rating | Early failure or unsafe operation | Wrong instrument rating | High | Open | 3 | Select correct range and rating | Match duty to actual process condition
CHK-020 | Selection | Verify hazardous area and enclosure requirements | Unsafe or non compliant installation | Wrong certification | High | Open | 3 | Use approved certified device | Confirm site classification before purchase
CHK-021 | Selection | Compare lifecycle cost, not only purchase price | Repeat breakdowns and high maintenance | Low cost poor fit | Medium | Open | 2 | Review total cost of ownership | Choose reliability over cheapest option
CHK-022 | Maintenance | Confirm calibration schedule is based on criticality | Long term drift or hidden error | Weak PM plan | High | Open | 3 | Revise PM frequency | Use service severity and history for planning
CHK-023 | Maintenance | Check seals, glands, covers, and breathers | Moisture ingress or corrosion | Weak preventive care | High | Open | 3 | Replace worn parts | Inspect weather related weak points routinely
CHK-024 | Maintenance | Review spares and repeat fault records | Repeat downtime on same loop | No failure learning | Medium | Open | 2 | Stock critical spares | Use root cause review for recurring faults
CHK-025 | Human Error | Validate DCS scaling and transmitter range | Impossible value on screen | Wrong configuration | High | Open | 3 | Correct scaling and verify settings | Use commissioning checklist for every loop
CHK-026 | Human Error | Verify polarity, wiring, and parameter entry | Device appears dead or reversed | Commissioning mistake | High | Open | 3 | Correct wiring and parameters | Do independent loop check before startup
CHK-027 | Human Error | Confirm temporary bypasses are removed | Unsafe or incorrect operation | Operator or startup error | High | Open | 3 | Remove bypass and restore logic | Track bypass status during startup
CHK-028 | Root Cause | Document failure symptom and actual cause | Same issue returns again | No root cause action | High | Open | 3 | Record and close RCA action | Use a repeat failure review process
CHK-029 | Root Cause | Track where the same fault repeats | Pattern of repeated breakdowns | Unresolved systemic issue | High | Open | 3 | Escalate repeated failures | Review equipment, installation, and process together
CHK-030 | Case Study | Check for plugged impulse lines in level loops | False high or false low level | Blocked line or sludge | High | Open | 3 | Clean line and improve flushing | Improve line routing and inspection
CHK-031 | Case Study | Check for grounding problems in noisy flow loops | Unstable flow reading | Poor shield or earthing | High | Open | 3 | Rework grounding practice | Verify cable routing and shielding
CHK-032 | Case Study | Check valve tuning when hunting appears | Oscillation and unstable control | Aggressive tuning or stiction | High | Open | 3 | Retune loop and service valve | Include valve health in PM
CHK-033 | Case Study | Inspect outdoor boxes after heavy rain | Trip or signal loss in rain | Water ingress | High | Open | 3 | Replace glands and seals | Use proper enclosure protection

## Lists
Category | Status | Priority | YesNo
Installation | Open | High | Yes
Environment | In Progress | Medium | No
Vibration | Closed | Low | N/A
Calibration
Electrical
Process
Selection
Maintenance
Human Error
Root Cause

## Summary
Instrumentation Failure Checklist Dashboard
Total Items | 33 | Category | Count
Open | 33 | Installation | 3
In Progress | 0 | Environment | 3
Closed | 0 | Vibration | 3
High Priority | 27 | Calibration | 3
|  | Electrical | 3
How to use
Filter by category, priority, or status
Update status as work progresses
Use remarks for field notes
Review high priority items first
Use the dashboard to track progress