## Checklist
Radar Level Transmitter False Echo Troubleshooting Checklist
Detailed field checklist for inspection, troubleshooting, echo curve review, and preventive maintenance
No. | Section | Checklist Item | What to Verify | Why It Matters / Risk | Status | Observation | Corrective Action | Priority
1 | General Process Verification | Confirm actual tank level with local gauge / sight glass if available | Cross-checks the transmitter against the real process condition | False reading may come from the process change, not the transmitter | Not Started |  |  | High
2 | General Process Verification | Verify whether the tank is filling, emptying, or holding steady | Level trend should match process movement | Wrong interpretation of movement can hide false echoes | Not Started |  |  | High
3 | General Process Verification | Check whether foam, splash, turbulence, or agitation is present | Process surface quality affects echo stability | Foam and turbulence can weaken or scatter the true echo | Not Started |  |  | High
4 | General Process Verification | Confirm product type and dielectric constant have not changed | Radar sensitivity changes with product dielectric | Low dielectric products create weak returns and more false echoes | Not Started |  |  | High
5 | General Process Verification | Check whether temperature, pressure, or vapor conditions changed | Process conditions can alter signal behavior | Changed process conditions can make the old echo map invalid | Not Started |  |  | Medium
6 | General Process Verification | Confirm recent maintenance or vessel modifications | Any change inside the vessel can alter reflections | New reflections may create strong fixed false echoes | Not Started |  |  | High
7 | Installation and Mounting | Verify transmitter is mounted at the correct nozzle / nozzle centerline | Mounting position controls beam path clarity | Wrong position can make the beam hit walls or internals | Not Started |  |  | High
8 | Installation and Mounting | Check distance from tank wall is within vendor recommendation | Wall reflections are a common false echo source | Too-close mounting can create a stronger wall echo than surface echo | Not Started |  |  | High
9 | Installation and Mounting | Confirm beam does not cross inlet stream, agitator, or moving internals | The beam should have an unobstructed path | Beam obstruction causes fluctuating or locked wrong reading | Not Started |  |  | High
10 | Installation and Mounting | Check nozzle length and internal diameter | Long narrow nozzles can act like reflection chambers | Nozzle reflection may dominate the true surface echo | Not Started |  |  | High
11 | Installation and Mounting | Inspect nozzle interior for rough surfaces, weld lips, or buildup | Rough nozzle surfaces create extra reflections | Unexpected internal reflections can generate a fixed echo peak | Not Started |  |  | Medium
12 | Installation and Mounting | Confirm sensor alignment is vertical and per vendor orientation | Misalignment changes beam target location | Tilt can push the beam toward the wall or internals | Not Started |  |  | High
13 | Installation and Mounting | Verify roof shape, cone, or domed geometry is not interfering | Tank roof geometry can reflect the signal | Roof reflections can confuse the transmitter during empty or low level | Not Started |  |  | Medium
14 | Antenna / Probe Condition | Inspect antenna face for dust, wax, film, coating, or crystallization | Contamination distorts the radiating surface | Dirty antenna reduces signal strength and accuracy | Not Started |  |  | High
15 | Antenna / Probe Condition | Check for condensation or moisture on antenna or probe | Moisture can attenuate or distort the echo | Wet antenna often causes unstable or drifting reading | Not Started |  |  | High
16 | Antenna / Probe Condition | Inspect for corrosion, pitting, or mechanical damage | Physical damage affects performance and reliability | Damaged antenna can create weak or malformed echoes | Not Started |  |  | High
17 | Antenna / Probe Condition | Confirm probe is not bent, twisted, or touching internals | Probe contact changes signal propagation | Contact with internals may create false reflections or no signal | Not Started |  |  | High
18 | Antenna / Probe Condition | Check for buildup on guided wave radar probe | Coating on probe changes reflected pulse behavior | Build-up can shift echo detection and cause level error | Not Started |  |  | High
19 | Antenna / Probe Condition | Verify antenna type matches the process service | Correct antenna selection improves echo quality | Wrong antenna can perform poorly in sticky or dusty service | Not Started |  |  | Medium
20 | Echo Curve Diagnostics | Open transmitter diagnostics and view echo curve | The echo curve shows the reflection profile | Without the echo curve, false echo diagnosis is slow and uncertain | Not Started |  |  | High
21 | Echo Curve Diagnostics | Check peak height of the surface echo | The true surface echo should be the dominant usable peak | Weak peak may allow a false echo to win | Not Started |  |  | High
22 | Echo Curve Diagnostics | Check peak position against actual level | Valid peak moves with actual process level | Fixed peak usually indicates wall, nozzle, or internal reflection | Not Started |  |  | High
23 | Echo Curve Diagnostics | Look for multiple peaks or duplicate reflections | Multiple reflections can confuse echo selection | Extra peaks may cause unstable or jumpy output | Not Started |  |  | High
24 | Echo Curve Diagnostics | Compare echo curve during normal operation and disturbance | Operating condition can reveal intermittent false echoes | Mixer start-up or filling can create problem echoes only sometimes | Not Started |  |  | Medium
25 | Echo Curve Diagnostics | Confirm transmitter is tracking the correct echo point | The selected peak must match actual level movement | Wrong peak selection is the main reason for bad output | Not Started |  |  | High
26 | Configuration and Mapping | Verify empty distance setting | Empty distance must match the tank geometry | Wrong empty distance gives wrong level scaling | Not Started |  |  | High
27 | Configuration and Mapping | Verify full distance / tank height setting | Full distance drives the upper scaling point | Incorrect value causes wrong 0–100% output | Not Started |  |  | High
28 | Configuration and Mapping | Check dead band and blocking distance | These settings prevent near-nozzle false tracking | Poor blocking distance can allow nozzle reflections to be used | Not Started |  |  | High
29 | Configuration and Mapping | Confirm output scaling matches the actual vessel | Output should align with the process range | Bad scaling creates incorrect DCS / PLC indication | Not Started |  |  | High
30 | Configuration and Mapping | Review false echo mapping data | Stored false echoes should match the current vessel condition | Old mapping may be invalid after modifications | Not Started |  |  | High
31 | Configuration and Mapping | Repeat mapping after cleaning, maintenance, or vessel change | Mapping should reflect the current installed condition | Skipping remap can leave the transmitter locked to an old false echo | Not Started |  |  | High
32 | Root Cause Review | Check for agitators, mixers, or moving blades in beam path | Moving internals can create intermittent false echoes | Agitator reflections often appear only during operation | Not Started |  |  | High
33 | Root Cause Review | Check for baffles, ladders, beams, coils, or dip pipes | Fixed internals are classic false echo sources | Any internal metal surface can return a strong echo | Not Started |  |  | High
34 | Root Cause Review | Check for inlet stream splashing into the beam zone | Filling stream can create surface turbulence | Splashes can create unstable echo detection | Not Started |  |  | High
35 | Root Cause Review | Check for foam layer thickness and density | Foam can absorb or scatter microwave energy | Radar may read foam top instead of liquid surface | Not Started |  |  | High
36 | Root Cause Review | Check for low dielectric hydrocarbon / solvent service | Low dielectric products produce weaker surface echoes | False echoes become more dominant in these applications | Not Started |  |  | High
37 | Root Cause Review | Check for recent process changes affecting echo quality | Product change may require new tuning / mapping | Old settings may no longer be valid | Not Started |  |  | Medium
38 | Preventive Maintenance | Clean antenna or probe at planned intervals | Clean sensors maintain signal quality | Slow drift often indicates contamination buildup | Not Started |  |  | High
39 | Preventive Maintenance | Inspect antenna and nozzle during shutdown rounds | Scheduled inspection catches early problems | Early detection prevents false alarm events | Not Started |  |  | Medium
40 | Preventive Maintenance | Review diagnostics trend during routine checks | Curve changes reveal emerging faults | Trend analysis helps identify buildup or new reflections | Not Started |  |  | Medium
41 | Preventive Maintenance | Reconfirm readings against local gauge after changes | Cross-verification prevents hidden measurement errors | Operator confidence depends on matching readings | Not Started |  |  | High
42 | Preventive Maintenance | Document mapping, calibration, and maintenance date | Good records speed up future troubleshooting | Missing records make future faults harder to resolve | Not Started |  |  | Low
43 | Preventive Maintenance | Train operators to report sudden jumps, frozen output, and false alarms | Operator feedback is often the first warning | Early reporting reduces downtime and misoperation | Not Started |  |  | Medium

## Quick Reference
Radar False Echo Quick Reference
Common causes, symptoms, and corrective actions for field troubleshooting
Cause / Symptom | What It Usually Looks Like | Primary Diagnostic Check | Best Corrective Action | Priority
Internal tank structure | Fixed wrong reading or intermittent jump | Compare echo peak against internal object location | Review mounting point and apply mapping | High
Long nozzle reflection | Reading stays fixed near one distance | Inspect nozzle length and nozzle diameter | Reduce nozzle effect or remap false echoes | High
Foam / turbulence | Noisy trend or unstable output during filling | Check process condition during operation | Improve process / tuning / damping settings | High
Antenna contamination | Slow drift over weeks or months | Inspect antenna face and coating | Clean sensor and re-verify echo curve | High
Low dielectric product | Weak surface echo and frequent wrong peak selection | Review product properties and curve strength | Tighten installation and mapping discipline | High
Agitator reflection | Wrong reading only when mixer runs | Observe echo curve during agitator operation | Reposition sensor / re-map under operating condition | High
Wrong scaling | Output does not match actual tank range | Check empty / full distance settings | Correct configuration and verify against vessel | High

## Summary
Checklist Summary Dashboard
Completion status and quick workbook overview
Total Checks | Done | In Progress | Not Started | N/A | Completion %
43 | 0 | 0 | 43 | 0 | 0%
Status Legend |  |  |  | Best Use Tips
Not Started | Checklist item not yet reviewed |  |  | 1 | Start with process verification before changing instrument settings.
In Progress | Work underway / partially verified |  |  | 2 | Use the echo curve to identify fixed reflections and level peaks.
Done | Verified and closed |  |  | 3 | Re-map false echoes after maintenance or vessel modification.
N/A | Not applicable for this vessel |  |  | 4 | Keep antenna, nozzle, and probe condition under routine inspection.